## Sheet1
Date |  | S4NT |  |  |  | Ref
29/09/2021 |  | PPM – Mechanical Check |  |  |  | ZEN-MC-7410
Calorifier Number: |  | 1 & 2 | Address: | Cheviot View , West Street, West Allotment, Newcastle upon Tyne, NE27 0RA
No | Task |  |  | Comments
1 | Calorifier ON/OFF |  | On | On.On
2 | If calorifier OFF, date when OFF |  | 01/01/1980
3 | If Calorifier is OFF, is it empty? (Y/N) |  | NA | N/A
4 | Circulation pumps ON/OFF |  | On | ON
5 | Shunt pumps ON/OFF |  | On | ON
6 | Are there any leaks (Y/N) |  | N | NO
7 | Condition of associated pipework and valves |  | Good | Signs of old leak on calorifier 2
8 | Condition of associated pumps |  | Good | Zone 1 , Primary and 2 destrat pumps
9 | Condition of initial drain water |  | Good
10 | Temperature of initial drain water (oC) |  | 27.7
11 | Is there sludge present (Y/N) |  | N
12 | Is Temperature stratification present (Y/N) |  | N
13 | Condition of insulation |  | Good
14 | Are temperature/pressure gauges operating OK |  | Y
15 | Water analysis carried out (Y/N) |  | N
16 | Analysis results |  | NA
17 | Full drain flush carried out (Y/N) |  | N
18 | Date Calorifier pasteurised/disinfected last |  | 01/01/1980
19 | Date of last 2 yearly inspection (where applicable) |  | 01/01/1980
20 | Expansion Vessels ok |  | Y
21 | Expansion Vessel charge |  |  | CW 3.9 x 2 heating vessel 1.6
22 | Pump Condition |  | Good | Zone 1 and primary pumps secondary pump and destrat pumps
23 | Pump Amps |  |  | Zone 1= 1.2 pump 2= 1.2. Primary 1= 2,2 Primary 2 =2.2 Destrat 1 = 0.3 . Destrat 2 = 0.3 Secondary =0.8
24 | Flue Condition |  | Average | Leaking condensate on some joints
25 | PRV Condition |  | Good | Not passing
26 | Safety device Condition |  | Good
Engineer Comments: BMS not operating
Name |  | Graham Parker | Signature |  | Date of Check | 29/09/2021