## Sheet1
Date |  | S4NT |  |  |  | Ref
29/10/2021 |  | PPM – Mechanical Check |  |  |  | ZEN-MC-7704
Calorifier Number: |  |  | Address: | Emmerson Court, Shiremoor, Newcastle Upon Tyne, NE27 0NG
No | Task |  |  | Comments
1 | Calorifier ON/OFF |  | On | On.On
2 | If calorifier OFF, date when OFF |  | 01/01/1980
3 | If Calorifier is OFF, is it empty? (Y/N) |  | NA
4 | Circulation pumps ON/OFF |  | On
5 | Shunt pumps ON/OFF |  | On
6 | Are there any leaks (Y/N) |  | Y | Ĺeaks on boiler and flue condensate pipe
7 | Condition of associated pipework and valves |  | Average
8 | Condition of associated pumps |  | Good
9 | Condition of initial drain water |  | NA
10 | Temperature of initial drain water (oC) |  | 16.9
11 | Is there sludge present (Y/N) |  | N
12 | Is Temperature stratification present (Y/N) |  | N
13 | Condition of insulation |  | Good
14 | Are temperature/pressure gauges operating OK |  | Y
15 | Water analysis carried out (Y/N) |  | N
16 | Analysis results |  | NA
17 | Full drain flush carried out (Y/N) |  | N
18 | Date Calorifier pasteurised/disinfected last |  | 01/01/1980
19 | Date of last 2 yearly inspection (where applicable) |  | 01/01/1980
20 | Expansion Vessels ok |  | Y
21 | Expansion Vessel charge |  |  | CW 3.5 x 2 heating vessel 4 bar
22 | Pump Condition |  | Good
23 | Pump Amps |  |  | Zone 1= 0.5 pump 2= 0.4.Zone 2 pump 2=0.9 pump 1 = 0.9 secondary pump = 0.6. Primary 1= 0.9 Primary 2 =0.9 Destrat 1 = 0.3 . Destrat 2 = 0.3
24 | Flue Condition |  | Good
25 | PRV Condition |  | Good
26 | Safety device Condition |  | Good
Engineer Comments:
Name |  | Tessa Aston | Signature |  | Date of Check | 15/10/2021