## Sheet1
Date |  | Castles & Coasts Housing Association |  |  |  | Ref
22/02/2022 |  | PPM – Mechanical Check |  |  |  | ZEN-MC-9525
Calorifier Number: |  | 1 | Address: | Pembroke Court , Hylton Lane, Downhill , SR5 4DF
No | Task |  |  | Comments
1 | Calorifier ON/OFF |  | On
2 | If calorifier OFF, date when OFF |  | 01/01/1980
3 | If Calorifier is OFF, is it empty? (Y/N) |  | NA
4 | Circulation pumps ON/OFF |  | On
5 | Shunt pumps ON/OFF |  | On
6 | Are there any leaks (Y/N) |  | Y | Leak on cold water tapping
7 | Condition of associated pipework and valves |  | Poor | Lockshield valves scaled , temperature gauge faulty Scale is starting to rot valves
8 | Condition of associated pumps |  | Average
9 | Condition of initial drain water |  | NA
10 | Temperature of initial drain water (oC) |  |  | 16
11 | Is there sludge present (Y/N) |  | N
12 | Is Temperature stratification present (Y/N) |  | N
13 | Condition of insulation |  | Poor | Missing and damaged in places
14 | Are temperature/pressure gauges operating OK |  | N | Faulty
15 | Water analysis carried out (Y/N) |  | N
16 | Analysis results |  | NA
17 | Full drain flush carried out (Y/N) |  | N
18 | Date Calorifier pasteurised/disinfected last |  | 01/01/1980
19 | Date of last 2 yearly inspection (where applicable) |  | 01/01/1980
20 | Expansion Vessels ok |  | Y
21 | Expansion Vessel charge |  |  | Cold water = 2 bar Heating = 2 bar
22 | Pump Condition |  | Average
23 | Pump Amps |  |  | VT = 0.7 PRIMARY HOT = 0.6 SHUNT = 2.1 + 2.5 DE STRAT = 0.5 SECONDARY RET = 0.3
24 | Flue Condition |  | Good
25 | PRV Condition |  | Good
26 | Safety device Condition |  | Good
Engineer Comments:
Name |  | Tessa Aston | Signature |  | Date of Check | 21/02/2022