## Sheet1
Date |  | Castles & Coasts Housing Association |  |  |  | Ref
04/08/2021 |  | PPM – Mechanical Check |  |  |  | ZEN-MC-5893
Calorifier Number: |  | 1 | Address: | Pembroke Court , Hylton Lane, Downhill , SR5 4DF
No | Task |  |  | Comments
1 | Calorifier ON/OFF |  | On
2 | If calorifier OFF, date when OFF |  | 01/01/1980
3 | If Calorifier is OFF, is it empty? (Y/N) |  | NA
4 | Circulation pumps ON/OFF |  | On
5 | Shunt pumps ON/OFF |  | On
6 | Are there any leaks (Y/N) |  | Y | Signs of leakage on cold fill pipework to calorfier,
7 | Condition of associated pipework and valves |  | Average
8 | Condition of associated pumps |  | Good
9 | Condition of initial drain water |  | Good
10 | Temperature of initial drain water (oC) |  | 61
11 | Is there sludge present (Y/N) |  | N
12 | Is Temperature stratification present (Y/N) |  | NA
13 | Condition of insulation |  | Average | Some insulation missing and not secure
14 | Are temperature/pressure gauges operating OK |  | N | Gauges broken
15 | Water analysis carried out (Y/N) |  | N
16 | Analysis results |  | NA
17 | Full drain flush carried out (Y/N) |  | N
18 | Date Calorifier pasteurised/disinfected last |  | 01/01/1980 | Na
19 | Date of last 2 yearly inspection (where applicable) |  | 01/01/1980 | Na
20 | Expansion Vessels ok |  | Y | Isolated and pressure checked , dhw 3.5 bat , heating 1.5 bar
21 | Expansion Vessel charge |  |  | Dhw 3.5 bar heating 1.5 bar
22 | Pump Condition |  | Good | Heating pumps all ok wilo yonos maxo 50/0.5ok grundfos today 80/120 twin set dhw pump grundfos up 20/45 ok primary pump grundfos ups 32/80 ok
23 | Pump Amps |  |  | 2.1 amp at speed 3
24 | Flue Condition |  | Good
25 | PRV Condition |  | Good
26 | Safety device Condition |  | Good
Engineer Comments: 2 x Remeha 210 gas ecopro visually checked all ok fluid automation pressurisation unit checked pump ok and operation ok
Name |  | Tessa Aston | Signature |  | Date of Check | 12/07/2021