## Sheet1
Date |  | S4NT |  |  |  | Ref
18/05/2022 |  | PPM – Mechanical Check |  |  |  | ZEN-MC-10883
Calorifier Number: |  | 2 | Address: | Moorcroft, Bowman Drive , Dudley, Newcastle upon Tyne, NE23 7FF
No | Task |  |  | Comments
1 | Calorifier ON/OFF |  | On
2 | If calorifier OFF, date when OFF
3 | If Calorifier is OFF, is it empty? (Y/N) |  | NA
4 | Circulation pumps ON/OFF |  | On
5 | Shunt pumps ON/OFF |  | On
6 | Are there any leaks (Y/N) |  | Y | Leaks on boiler condensate pipe work which has dropped on to prv pipe work and rotted through
7 | Condition of associated pipework and valves |  | Average
8 | Condition of associated pumps |  | Good
9 | Condition of initial drain water |  | Good
10 | Temperature of initial drain water (oC) |  | 40
11 | Is there sludge present (Y/N) |  | N
12 | Is Temperature stratification present (Y/N) |  | N
13 | Condition of insulation |  | Average
14 | Are temperature/pressure gauges operating OK |  | Y
15 | Water analysis carried out (Y/N) |  | Y
16 | Analysis results |  | Pass | PH7.8 @40 degrees
17 | Full drain flush carried out (Y/N) |  | N
18 | Date Calorifier pasteurised/disinfected last
19 | Date of last 2 yearly inspection (where applicable)
20 | Expansion Vessels ok |  | Y | Please see report
21 | Expansion Vessel charge |  |  | Please see report
22 | Pump Condition |  | Good
23 | Pump Amps |  |  | Please see report
24 | Flue Condition |  | Poor | Welds starting to show signs of distress
25 | PRV Condition |  | Good
26 | Safety device Condition |  | Good
Engineer Comments:
Name |  | Graham Parker | Signature |  | Date of Check | 18/05/2022