## Sheet1
Date |  | Castles & Coasts Housing Association |  |  |  | Ref
03/06/2024 |  | PPM – Mechanical Check |  |  |  | ZEN-MC-22111
Calorifier Number: |  | 2 | Address: | Cragside Court, Off Cragside Gardens, Gateshead, NE11 0AW
No | Task |  |  | Comments
1 | Calorifier ON/OFF |  | On
2 | If calorifier OFF, date when OFF |  | 01/01/1980
3 | If Calorifier is OFF, is it empty? (Y/N) |  | NA
4 | Circulation pumps ON/OFF |  | On
5 | Shunt pumps ON/OFF |  | NA
6 | Are there any leaks (Y/N) |  | N
7 | Condition of associated pipework and valves |  | Good
8 | Condition of associated pumps |  | Good
9 | Condition of initial drain water |  | Good
10 | Temperature of initial drain water (oC) |  |  | 56
11 | Is there sludge present (Y/N) |  | N
12 | Is Temperature stratification present (Y/N) |  | N
13 | Condition of insulation |  | Good
14 | Are temperature/pressure gauges operating OK |  | Y
15 | Water analysis carried out (Y/N) |  | Y
16 | Analysis results |  | NA | Awaiting results
17 | Full drain flush carried out (Y/N) |  | N
18 | Date Calorifier pasteurised/disinfected last |  | 01/01/1980 | N/a
19 | Date of last 2 yearly inspection (where applicable) |  | 01/01/1980 | N/a
20 | Expansion Vessels ok |  | Y
21 | Expansion Vessel charge |  |  | Please see report
22 | Pump Condition |  | Good
23 | Pump Amps |  |  | Please see report
24 | Flue Condition |  | Good
25 | PRV Condition |  | Good
26 | Safety device Condition |  | Good
Engineer Comments:
Name |  | Nick Heede | Signature |  | Date of Check | 15/05/2024