## Sheet1
Date |  | <CLIENT> |  |  |  | Ref
2021-05-25 |  | Domestic Hot Water Calorifier General Inspections |  |  |  | ZEN-MC-250
Calorifier Number: |  |  | Address:
No | Task |  |  | Comments
1 | Calorifier ON/OFF
2 | If calorifier OFF, date when OFF
3 | If Calorifier is OFF, is it empty? (Y/N)
4 | Circulation pumps ON/OFF
5 | Shunt pumps ON/OFF
6 | Are there any leaks (Y/N)
7 | Condition of associated pipework and valves
8 | Condition of associated pumps
9 | Condition of initial drain water
10 | Temperature of initial drain water (oC)
11 | Is there sludge present (Y/N)
12 | Is Temperature stratification present (Y/N)
13 | Condition of insulation
14 | Are temperature/pressure gauges operating OK
15 | Water analysis carried out (Y/N)
16 | Analysis results
17 | Full drain flush carried out (Y/N)
18 | Date Calorifier pasteurised/disinfected last
19 | Date of last 2 yearly inspection (where applicable)
20 | Expansion Vessels ok
21 | Expansion Vessel charge
22 | Pump Condition
23 | Pump Amps
24 | Flue Condition
25 | PRV Condition
26 | Safety device Condition
Engineer Notes
Signature |  |  |  |  | Date of Check

## Sheet1 (2)
All reported faults to be communicated
PPM System CALORIFIERS GENERAL INSPECTIONS COMPLETION INSTRUCTIONS FOR THE TASKS DESCRIBED IN FORM No. 9 (i) Advise Maintenance Supervisor of any defects found during monitoring work. (ii) Follow the Site’s procedures for confined spaces. (iii) Record all monitoring results and data in a neat and legible fashion. N.B. CALIBRATED EQUIPMENT ONLY TO BE USED
No: | Tasks | Comments
1 | Calorifier ON/OFF | Ensure operational status of Calorifier by checking the status of the associated isolation valves
2 | If OFF, date when OFF | If the Calorifier is OFF, indicate the date it came Off-line
3 | If Calorifier if Off, is it empty? (Y/N) | Confirm status of Inlet Valve
4 | Circulation pumps ON/OFF | Confirm the operational status of the circulation pump(s)
5 | Shunt pumps ON/OFF | Confirm the operational status of the shunt pump(s)
6 | Are there any leaks (Y/N) | Visually inspect Calorifier and associated valves for leaks
7 | Condition of assoc. Pipework and valves | Visually inspect all pipework for signs of corrosion and leaks, and visually inspect the condition of insulation fitted. Visually inspect all valves for correct operation, signs of corrosion and leaks
8 | Condition of assoc. pumps | Visually inspect all pumps fitted for correct operation and leaks
9 | Condition of initial drain water | Isolate CW feed and open drain point into a bucket and collect approximately the 1st litre of water discharged. Measure and record the condition, viscosity and colour of this water.
10 | Temp. of initial drain water (oC) | Measure and record the temperature of the water collected (remember to carry out biological analysis test first)
11 | Is there sludge present (Y/N) | See 9
12 | Is Temp. Stratification present (Y/N) | Using a contact thermometer, measure and record the temperature of the calorifier at; the top, middle and bottom. If there is more than 5oC difference between the top temperature and the bottom temperature then the calorifier is suffering from temperature stratification. If a contact thermometer cannot be used, then measure and record the difference in the “flow” temperature and the “drain” temperature.
13 | Condition of insulation | Visually inspect the insulation for signs of wear and tear and areas where the insulation has been removed
14 | Are temp./pressure gauges operating OK | Visually inspect that any gauges fitted are operating correctly. Compare against calibrated instruments.
15 | Water analysis carried out (Y/N) | Carry out biological analysis sample (Legionella sp.) on the water collected from the drain point.
16 | Analysis results | Obtain results from lab and complete log-sheet
17 | Full drain flush (Y/N) | Open the CW feed valve and then open the drain point allowing enough water to flow through so that any water discoloration is removed.
18 | Date Calorifier pasteurised last | Indicate the date that the calorifier was last pasteurised and indicate whether it was disinfected as routine or due to adverse conditions
19 | Date of last 2 yearly inspection | Indicate the date of the last insurance inspection