## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Burn Promenade
Burn Park Road
Houghton-Le-Spring
DH4 5EJ
CARRIED OUT ON BEHALF OF
Castles & Coasts Housing Association
REPORT NUMBER: 20-2671
DATE OF REPORT: 17/11/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-2671
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Castles & Coasts Housing Association
Address | Arcadia House
Balliol Business Park
Newcastle Upon Tyne
NE12 8EW
Site Address | Burn Promenade
Burn Park Road
Houghton-Le-Spring
DH4 5EJ
Carried Out On | 14/09/2020, 17/09/2020, 18/09/2020
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
Zenith-Service -TCH - CCGS1020 Karbon Gas Service Oct 2020

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-2671
SECTION 3: Report
0810- Attended site and carried out commercial gas tightness test , as per guidance in UP1A. The gas meter is a boundary meter located in a brick built meter House, that is kept locked. Traced pipework along its entire , then calculated the volume . Northern gas services have been contacted as PE pipework is exposed in a public walkway , they are attending today JOB REF NO , 5347 3021. Warning advice label is present , the gas transporters ECV is free moving. There are 2 x AECV'S fitted to the pipe work located in different areas both are seized solid and handles have been removed , ( 1 x on outlet side of gas meter and 1 x in the plantroom ) There is also a gas solenoid valve present on the pipework , but the actuator is missing . There is an emergency stop button fitted at the plantroom door , with tape over the button and a note beneath stating BUTTON NOT IN USE. The gas pipework from the meter into the plantroom is 3 " steel that is threaded and not welded . There is also a brass thumb tap fitted to the pipework , just after the solenoid valve . I do not know if this fitting is gas approved or not , its capped off and not leaking , I also don't know what the purpose of it is ( see media attached ) As the saftey features have been bypassed and are not working the installation is AT RISK and a warning notice has been issued . Pipework Volume IVP , 0.162 m3 IVF , 0.0162 m3 IVP , 0.100 m3 Total - 0.2782 m3 SOP > 60 m3 MAPD - 3.9 mb Let by , 2 minutes Stabilisation , 6 minutes TTP , 2 minutes Result Pass , zero drop recorded or detected with appliances connected. Attended site and carried out annual commercial gas saftey inspection . The gas appliances consist of 2 x open flue (B23) Potterton boilers , that supply DHW & CH to the building . Both appliances have been tested for safe operation , as per manufacturers instructions with all 26.9 checks carried out . Boilers are connected to a common flue system, that runs vertically through the building . The flue is showing signs of corrosion in various areas. Part of the flue cannot be inspected as it it in a duct , without inspection hatches or a Co alarm. The top half of the flue can be visually inspected , as loft hatch is in flat 15 , I have gained access today. The boilers are open flue but fan assisted , so the flue is under positive pressure . The flue now has non mechanical traps fitted , as prior it was not trapped . There is evidence of repairs and condensate stai g on the floor below . The installation is AT RISK and a warning notice has been issued . A Co detector has been installed on the landing as a safe measure , and the site manager "John " has been informed of its purpose The combustion and cooling ventilation is supplied via 2 x metal Louvred doors , that both communicate directly to outside. The fly screens have been removed prior to my visit , the doors do not have a true high and low definition. The doors supply adequate combustion and cooling ventilation for the appliances currently installed. The gas pipework is fully identified within the plantroom and well supported, with test points fitted working pressure ok as tested. A Warning Notice has been issued for the pipework already . Appliance Infotmation Boiler 1 LHS Potterton EC THREE 215 Sn , 14111714 GFA High fire 02 , 4.7 Co2 , 9.2 Co , 38 ppm Ratio , 0.0004 Low fire 02 , 4.7 Co2 9.2 Co , 13 ppm Ratio , 0.0001 Boiler 2 RHS Potterton EC THREE 215 Sn ,14115300 GFA High fire 02 , 4.9 Co2 , 9.1 Co ,13 ppm Ratio , 0.0001 Low fire 02 , 4.8 Co2 , 9.1 Co ,7 ppm Ratio , 0.0001 Burners have not been removed as gaskets not present , good GFA readings and flame picture .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-2671
SECTION 4: Photos
Room / Area
Description
Notes
Button not in use
Room / Area
Description
Notes
Gas solenoid valve
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-2671
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-2671
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-2671
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-2671
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes