## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Chapelville
Front Street
Seaton Burn
NE13 6EH
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 20-3621
DATE OF REPORT: 14/09/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-3621
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Chapelville
Front Street
Seaton Burn
NE13 6EH
Carried Out On | 06/10/2020
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-3621
SECTION 3: Report
0825- Attended site and carried out commercial gas tightness test as per guidance published in UP1A. Traced pipe work along entire route , to allow calculation of total volume. The gas meter is a boundary meter and is located in a ventilated plastic housing , that is kept locked . The meter location is to the RHS s of the plantroom , in the front garden . Gas pipe work is identified , and the warning advice label is present at the meter . The securing screw/bolt is missing from the gas wheel head isolation valve ( head on floor when accessed meter today ) , so when isolating the gas supply the wheel head falls off the spindle. I have reported this to northern gas network , for them to attend and retify ( REF NO , 5349-1284) All AEVS operate smoothly but not all fall to the closed position. Gas pipework has an earthing strap fitted in the plantroom, but not at the meter . IVP , 0.1188 M3 IVF , 0.01188 M3 IVM , 0.100 ( G40) TOTAL - 0.23068 M3 S.O.P. > 60 M3 MAPD - 4.0 MB Let by - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result Pass , zero drop recorded or detected with appliances connected. Carried out annual gas saftey inspection as req , appliances tested as per manufacturers instructions, along with all 26.9 checks to ensure safe operation. The gas appliances consist of 2 x hamworthy fleet modular boilers, and 2 x Lochinvar ecoshield water heaters . All appliances are open flue (B23) and are all connected to a common flue system . Only 1 x of the water heaters is working ( no.2 RHS) as no.1 LHS reqs parts and is acting as a buffer vessel . The burners on the 2 x hamworthy appliances have been removed , inspected with Gaskets and probes being replaced . Both burners req replacing on the boilers , but are operating safely at this moment in time . The burners have not been removed from the water heaters , for fear of damaging burner gaskets etc. Each appliance has been tested in both high and low fire modes , all readings recorded. The flue manifold has been drilled by a previous contractor to carry out GFA , there is no need for this as a test point is fitted to the front of the sumps. I have fitted Regin flue test point blanks , both to the boilers and the water heaters . The flue is well supported along its route , with slight signs of corrosio present . It has non mechanical traps fitted , formed out of fittings . The enters a brick built chimney , I do not know if the chimney is lined or not , or know the condition of the liner if present . The ventilation for combustion and cooling purposes is supplied via , louves at high and low levels in the plantroom door . There is also a large vent in the wall at high level , fly screens are fitted to the high level vent , but these are pea size The ventilation in place is adequate for the appliances, currently installed . There is an emergency stop button at the plantroom door , when pressed the gas supply to area is isolated , via solenoid valve . The controls are auto resetting and not manual , this is an existing installation. All AECVS are smooth operating and function , not all fall to the closed position. Appliance details Top module no.1 Hamworthy Fleet F125V Sn , F12VF141GB-01035F GFA high fire 02 , 4.9 Co2 , 9.1 Co , 64 ppm Ratio , 0.0005 Low fire 02 , 5.0 Co2 , 9.0 Co , 6 ppm Ratio , 0.0001 Bottom module no.2 Hamworthy Fleet F125V Sn , F12VF1141 - 01034F GFA high fire 02 , 5.0 Co2 , 9.0 Co , 72 ppm Ratio , 0.0008 Low fire 02 , 5.1 Co2 , 8.9 Co , 16 ppm Ratio , 0.0002 Water heater no.1 LHS Lochinvar SHW60 - 325CE Sn , K14C20074552 not tested as not currently running . Water heater no.2 RHS Lochinvar SHW60 - 325CE Sn , K14C20074551 GFA High fire 02 , 5.3 Co2 , 8.9 Co , 39 ppm Ratio , 0.0004 Low fire 02 , 5.2 Co2 , 8.9 Co , 14 ppm Ratio , 0.0002

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-3621
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-3621
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-3621
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-3621
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-3621
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes