## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Police House
Glebe Terrace
Scorton
DL10 6DL
CARRIED OUT ON BEHALF OF
HG Morgan Sindall
REPORT NUMBER: 20-4519
DATE OF REPORT: 24/05/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-4519
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | HG Morgan Sindall
Address | Sheffield South
Yorkshire
S9 2UB
Site Address | Police House
Glebe Terrace
Scorton
DL10 6DL
Carried Out On | 28/10/2020
Survey Completed By | Dave Aston
SECTION 2: Introduction
Job Description - Repaire HRM WALLSTAR boiler, suspect prv / vessel issue.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-4519
SECTION 3: Report
Arrive onsite 0820 Tennant informed me that the boiler wouldn't fire so they have no heating or hot water. The boiler is a HRM WALLSTAR oil combi boiler , carry out initial checks and find boiler oil feed full of air purge through from oil storage tank through to the tiger loop de-ariator, then purge burner pump , boiler now firing up but found to be sooty, had to contact manufacturer for instructions to set up. Using manufacturer's instructions set the oil pressure to 105psi and the co2 to 9.7 boiler now firing ok and isn't sooty, I haven't touched any thing else on the boiler but the tennant has heating and hot water now. This boiler is in poor condition and is 15 + years I am advising that this is replaced for new boiler either another wall hung combi as a direct replacement or a floor standing heat store boiler in the same out house, this could be linked in to the second system making the system in to one allowing removal of both wall hung oil fired combi boiler. Whilst in the property using the heating controls I found the room stat (honeywell t6360) to be faulty wouldn't switch every time so i have linked this out and informed the tennant to contact his landlord that this needs replacing Left site all working Parts used 2 x 3/8" oil 'on rings from van stock 1 x roll of blue roll Off site 11.00 complete

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-4519
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-4519
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-4519
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-4519
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-4519
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes