## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Pembroke Court
Hylton Lane
Downhill
SR5 4DF
CARRIED OUT ON BEHALF OF
Castles & Coasts Housing Association
REPORT NUMBER: 20-4896
DATE OF REPORT: 21/04/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-4896
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Castles & Coasts Housing Association
Address | Arcadia House
Balliol Business Park
Newcastle Upon Tyne
NE12 8EW
Site Address | Pembroke Court
Hylton Lane
Downhill
SR5 4DF
Carried Out On | 10/11/2020, 23/11/2020
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
Commercial Boiler Service

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-4896
SECTION 3: Report
0820 - 1210 Attended site and carried out annual gas saftey inspection , all 26.9 checks carried out and tested as per manufacturers instructions. Burners have not been removed as Gaskets will be req . The gas appliances consist of 2 x open flue Remeha Gas 210 Eco Pro Boilers, that supply DHW & CH to the building. The 2 x Boilers are in poor physical condition , as are both of their flues. Boiler no 1 LHS has had a temporary repair carried out to the Heat Exchanger , this was not carried out by myself. I can only assume that heat resistant silicone has been used on the Heat Ex , directly above the burner . I do not know what product has been used on the repair , but looking at it , it was carried out some time ago . The silicone product could break down and fail at any time , and possibly leak Products of Combustion . I have tested for leakage of gas and products around the temp repair , but found to be clear at this time of testing . Boiler no 2 RHS has had one of the burner studs removed , and a bolt fitted in its place. This is a common fault with this appliance , as the burner stud threads in the heat ex easily strip. The stud currently fitted is not the correct bolt , but it is holding the burner solidly and is creating a good seal. A new longer threaded stud is req . Both flues are showing significant signs of corrosion , with silver foil tape wrapped around joints . Flue not currently leaking , but could fail in the near future . Combustion and cooling ventilation is supplied via 2 x large metal Louvred doors . Both doors communicate directley to outside . Both doors have solid fly screens fitted to them , the screens do not conform to BS6644 as they are too small The screens cannot be easily removed and are clearly prone to blocking . There is an existing stop button fitted next to the plantroom door, when pressed the gas supply is isolated to the area. There is a gas solenoid interlocked to the gas supply , the controls are manually reset and not auto ( working ok as tested ) Appliance details Boiler no 1 LHS Remeha Gas 210 eco pro Sn , 1013102798070 GFA High fire 02 , 5.4 Co2 , 8.8 Co , 19 ppm Ratio, 0.0002 Low fire 02 , 4.6 Co2 , 9.2 Co , 62 ppm Ration, 0.0007 Boiler no 2 RHS Remeha Gas 210 eco pro Sn , 1015302801160 GFA High fire 02 , 5.0 Co2 , 9.0 Co , 25 ppm Ratio , 0.0003 Low fire 02 , 4.6 Co2 , 9.2 Co , 26 ppm Ratio , 0.0003 warning notice issued as AT RISK. Gas pipe work not tested as of yet Second visit of the day 1430 -1510 Collect materials to carry work to secure burner on boiler no.2 1530 -1630 Fit threaded bar to bottom LHS burner location thread on boiler no2 . Cut 8 mm threaded bar down to correct size . Locked into place with thread lock , allowed time to cure . Fitted correct skirted nut and correct bolt to fan assembly Refined burner and fully tightened up and now secure in place . Gas tightness test still to be carried out . LPC 23.11.20 0810 - 1430 Attended site and carried out commercial gas tightness , as per guidance published in UP1A. Traced gas pipe work along its entire to allow calculation of the volume . The gas meter ( G25 / U40 ) is located in a brick built meter House next the plantroom . The meter House is well ventilated and is kept locked the combination for the lock is 1973 . The code for the lock is written on the control panel within the plantroom. Both the ECV and AECV are free moving , complete with label of operation. The warning advice notice is also present within the meter House. The gas pipe from the meter is significantly corroded, as it has not been painted for protection. Also the gas pipe work is not sleeved through the wall. I have checked along the length of the pipework, it isn't earth bonded at any point. The pipe work within the plantroom is well supported and identified with test points fitted. This gas meter / pipework only supplies the 2 x boilers in the plantroom, as it terminates here. Due to the fact that the pipework is corroded , not earthed or sleeved , the installation is AT RISK - a warning notice has been issued . IVP - 0.0288 m3 IVP - 0.00288 m3 IMV - 0.067 m3 Total - 0.09868 m3 SOP - The plantroom - 50 m3 MAPD - 3.5 mb Let by - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result Pass , zero drop detected or recorded with appliances connected . Carried out annual gas saftey inspection on 2 x communal domestic boilers, burners have not removed. Both appliances have their own U6 domestic gas meters and domestic gas pipework Communal boiler no.1 - Laundry room Boiler is located in the laundry room next to flat no.41, the domestic gas meter is located directly below the boiler in a cupboard. Tested the appliance for safe operation as per manufacturers instructions , along with all 26.9 checks carried out . Found that both flue sample point plugs are broken , and consequently do not form a complete seal . There is clear evidence of products of combustion leaking , as staining to top of appliance . This is IMMEDIATELY DANGEROUS situation. I made the appliance safe and left site, called to a local suppliers and collected new sample point caps. Returned to site and fitted new sample point cap to the appliance as req. Carried out domestic tightness test as per , found to be gas tight . Warning advice label is present , ECV is accessible and free moving with label of operation present . Appliance details Potterton Promax 28 combo erp Sn , 7219455 GC no - 47.393.48 GFA High fire 02 , 5.5 Co2 , 8.7 Co , 59 ppm Ratio , 0.0007 Low fire 02 , 6.1 Co2 , 8.4 Co , 30 ppm Ratio , 0.0004 Communal boiler no.2 - Bin Store The other domestic communal boiler is located in the bin store area next to flat no.31. The appliance is room sealed , the flue terminal guard is completely rotten , as boiler is condensing . A new nylon coated condensing proof terminal guard has been fitted today. The gas meter is situated directly outside the bin , next to the door The ECV is accessible and free moving with label of operation , the warning advice notice is also present . The gas pipe work from the meter is sealed through the wall , with non setting compound , the meter is also earthed . Carried out domestic gas tightness test as per UP1B , found to tight . Appliance details Potterton Promax 30 SL Sn , DNG1331600017DC GFA High fire 02 , 4.9 Co2 , 9.1 Co , 40 ppm Ratio , 0.0004 Low fire 02 , 5.7 Co2 , 8.6 Co , 33 ppm Ratio , 0.0004

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-4896
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-4896
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-4896
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-4896
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-4896
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes