## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Haven House
Valley View
Leadgate
DH8 7PS
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-4907
DATE OF REPORT: 11/01/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-4907
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Haven House
Valley View
Leadgate
DH8 7PS
Carried Out On | 11/01/2021 05/01/2021 13/11/2020
Survey Completed By | Dave Aston
SECTION 2: Introduction
AGSC

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-4907
SECTION 3: Report
LPC - 13.11.20 1245 - 1600 Arrived on site and gained access to plantroom, an ideal is fitted . The appliance is supplied by a U16 gas meter , located on the grass areas , in a plastic meter House. The gas pipe work enters the plantroom, feeds the boiler then tees off in 22 mm copper and runs a ceiling level. The pipe work then exits the plantroom vertically and then disappears. The pipe work is not labelled stating what area its supplying. Each flat had their own boilers, gas cookers and individual gas meters . Checked to see if there is there is wardens flat , off the commercial meter . The manager is not aware of any other commercial communal gas appliances on site . There is not a line drawing on site , to assist with tracing pipe work . We have searched the site to see if there is a gas cooker or a combi in the kitchen area . We have also gained access on to the main room area , see if there is a AHU installed . Gained access to the guest room , and again no gas appliances. Checked the laundry for a gas fired dryer , each appliance is electric . We can inly assume that the pipe work is running in the unventlated boxing , directly above point of exit in the plantroom . This could be running anywhere , unidentified and live . I have not worked on the boiler or the gas pipe work today. Joiners will be req to remove the boxing above the plantroom , in an attempt to locate the pipe. If the pipe is not used the best option would be to cap if off within the plantroom area , then purge the line. A warning notice has been issued as AT RISK. before any further work can take place, the issue with the pipe reqs sorting first . Dave Hunter LPC 5.1.21 1130 - Attend site with Lee chaterton 11.30 to carry out service and tightness test Cut sections in boxing in out using multi tool to trace pipework, find it leads to main corridor ceiling void so strip out ceiling lights to see where 22mm gas pipework is located(using phone cameras) trace pipework to kitchen , take out kitchen cuboards to locate gas pipe which is capped off. Strip out pipework in plantroom, and using hosepipe in kitchen attached to gas pipe purge the gas out of the pipe using air, once the gas pipe proved to be gas free , cap off in the plant room and strip back redundant pipework. Replace all ceiling lights and refit all kitchen cuboards tidy site. Start to service boiler find flue damaged order parts Offsite 1630 Attend site 1230 11/01/21 Strip boiler down and replace internal flue in boiler and all the external flue to outside as the flue is badly corroded. Flue position is not 300mm from an internal wall. Strip burner out and flush heat exchanger out clean boiler sump of all debris clean condensate trap, replace gaskets and also ignition probes. Only one boiler on site Once all reassembled commission and test. Co2 high 8.9% co 59ppm ratio 0005 Co2 low 8.0% co 13ppm ratio 0001 Carry out a tightness test meter is in garden above plantroom . System is .030m3 with a G10 meter Test is 2 mins 6 mins 2 mins 0 mbar drop Pumps all working and 3 port on DHW cylinder all working controls all ok

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-4907
SECTION 4: Photos
Room / Area
Description
Notes
The complete flue has been replaced
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-4907
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-4907
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-4907
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-4907
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes