## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Oakwood Court
Stanley
County Durham
DH9 8NE
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5245
DATE OF REPORT: 19/03/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5245
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Oakwood Court
Stanley
County Durham
DH9 8NE
Carried Out On | 19/11/2020, 20/11/2020, 03/12/2020, 15/03/2021, 19/03/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
Gas line issue picked up on AGSC (20-4902)

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5245
SECTION 3: Report
LPC 19.11.20 1005 -1200 Met on site with northen gas to discuss possibility with renewing main Gas ECV to site . On going works LPC + DA 20.11.20 1050 - 1135 . Recived a phone call this morning from Mark from Northen Gas , request that I can attended to allow access to gas meter for further investigation . Arrived on site and gave Mark and the Welder access to the gas meter , and discussed further . Risk assessments to be produced and supplied by Northen gas . Dave Aston was on site today assisting myself with works , he has been brought up to speed with issues on site . Northen gas are looking to carry out the valve swap works next Wednesday 25.11.20 to be fully confirmed on monday . LPC 3.12.20 1310-1530 Recieved phone call this morning from Mark of Northern Gas , requesting a site visit . Attended site as req and met with Mark and their pipe work contractor . Discussed further a possible resolution to fitting a new ECV and possible route of pipe work . Allowed access via keys on site , locked up when completed. LPC - CS 15.2.21 0830 - 1230 Got confirmation early this morning that the gas supply works , is being started today . Met on site with northen gas Networks, agreed locations of walkways etc. This is an ongoing job that will req my or Dave Astons attendance each morning. LPC - CS 19.3.21 0830 - 1700 Arrived on site isolated all gas appliances and shut down gas supply after the gas meter , kept the gas line under positive pressure . Northen gas Networks ran in their external supply , whilst the welder began assembling the new internal supply . Another engineer attended from northen gas Networks, to re commission the gas meter , was not happy with the ECV position . Welder returned to after the new gas line had been primed with gas . Entire new gas supply has to be removed and altered with a new extra ECV fitted . Then after the pipe work had cooled and the welder had left , a gas leak was found on the new pipework. Pipe work again had to be removed and repaired. Finally got the gas supply back on the building, gas tightness test of sections was carried out by northen gas , this time all found to be tight . Turned all appliances back on and fired up , tested working pressure as new supply smaller than original supply . Found working pressure both at the meter and at the boilers to be all ok . Allowed appliances time recover both CH & DHW , pulled water through to taps. Checked all CH through the building again all ok . Cleaned up after contractors left site , returned all keys and locked up .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5245
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5245
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5245
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5245
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5245
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes