## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
The Elms
Chester-Le-Street
County Durham
DH2 3EJ
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5428
DATE OF REPORT: 11/01/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5428
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | The Elms
Chester-Le-Street
County Durham
DH2 3EJ
Carried Out On | 01/12/2020, 11/01/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 28.01.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5428
SECTION 3: Report
LPC 1.12.20 0820 - 0920 Items req to carry out works 5 X remeha quinta pro 115 service kit A 1 x 1 1/2 inline non mechanical trap 2 x gas test nipple 1 x 1/4 x 3/4 Bush 1 x 1/4 × 1/2 Bush Parts orderd with Steve at Parts Centre Silverlink . NOTE ..... I have not worked on or tested Boilers , gas pipe work , today . LPC 11.1.21 0820 - 1610 Attended site and carried out annual commercial gas saftey inspection on 5 x open flue ( B23) Remeha boilers . Each burner has been removed , heat exchanger cleaned and inspected . Found all burners to be worn and would reccomend, replacing next year . Gaskets and probes have been replaced , appliances tested as per manufacturers instructions. All 26.9 saftey checks also carried out . There is also a gas fired engine (CHP) on site , this has not been tested or worked on today . The CHP is on it's own separate gas Certificate as tested and issued by the manufacturer. The CHP is not currently in use as it has a leak on the flue externally. The engine has it's own separate flue . I have included the engine when calculating the req and actual ventilation. Combustion and cooling ventilation is supplied via 2 x large metal Louvred doors , they do not have high and low definition. Both doors communicate directley to outside, they supply more than adequate ventilation as calculated. All 5 x boilers are connected to a common flue header , that is in good physical condition. The flue has condensate lines , with non mechanical traps fitted. The condensate lines to each individual flue turrent in the boilers , have been sealed with black flue sealant . The sealant seems to be in good condition , as not leaking currently, I cannot guantee its longevity. One of the condensate lines after the trap is tapped up , this is not a proper permanent fitting . These repairs seem to be temporary repairs , but have not be returned on to fully completed . Warning notice has been issued and a Co detector has been installed as a safe measure. The flue then runs externally up the rear side of the building . There is an emergency stop button at the plantroom door , when pressed the gas supply is isolated to the area . The controls are manually resetting, this is working ok as tested . There is a gas ECV fitted to the power work upon entry to the area. Pipe work is fully identified and supported along its route. Purge and test points are fitted , each appliance has it's own manufacturers isolation valve fitted. Appliance details Boiler no 1 Remeha Quinta pro 115 Sn , 1502610837430 GFA High fire 02 , 4.4 Co2 , 9.4 Co , 68 ppm Ratio , 0.0007 Low fire 02 , 6.1 Co2 , 8.4 Co , 14 ppm Ratio , 0.0002 Boiler 2 Remeha Quinta pro 115 Sn , 1501410743820 GFA High fire 02 , 4.5 Co2 , 9.3 Co , 67 ppm Ratio , 0.0007 Low fire 02 , 6.0 Co2 , 8.4 Co , 15 ppm Ratio , 0.0002 Boiler 3 Remeha Quinta pro 115 Sn , 1502610837390 GFA High fire 02 , 4.3 Co2 , 9.4 Co , 77 ppm Ratio , 0.0008 Low fire 02 ,5.9 Co2 , 8.5 Co , 6 ppm Ratio , 0.0001 Boiler 4 Remeha Quinta pro 115 Sn , 1502610837200 GFA High fire 02 , 4.3 Co2 , 9.4 Co , 72 ppm Ratio , 0.0008 Low fire 02 , 6.1 Co2 , 8.4 Co , 22 ppm Ratio, 0.0003 Boiler 5 Remeha Quinta pro 115 Sn , 1502610837610 GFA High fire 02 , 4.1 Co , 9.5 Co , 66 ppm Ratio, 0.0007 Low fire 02 , 6.0 Co2 , 8.5 Co , 10 ppm Ratio , 0.0001 CHP UNIT EC / SAV XRG19 Sn , 11 14 00 0148 Not tested or worked on today , unit not in use as condensate from external flue leaking on to gas pipe work below . Carried out commercial gas tightness test as per the guidance published in UP1A. The gas meter is a boundary meter , located in the side garden area . The meter is housed in a purpose built plastic cover , that is kept locked . The gas transporters warning advice label is present, but it has not be completed by the installer . So information regarding MOP etc is not known . The gas ECV/ Wheel head valve is smooth operating, as is the AECV on the outlet side of the meter . A test point has been fitted at the meter today , as the only test point was within the plantroom area. Traced and calculated the volume , inorder to carry out the test . There is a secondary meter installed that is used to monitor gas used by the CHP unit only . IVP - 0.36 m3 IVF - 0.036 m3 IMV , 0.100 m3 Total - 0.496 m3 S.O.P - the plantroom > 60 m3 MAPD - 3.7 mb Let by- 2 minutes Stabilisation - 6 minutes TTP - 4 minutes Result.... Pass , zero drop detected or recorded with appliances connected. Tested all plant etc Found to be an issue with shunt pumps , quotation obtained from total pumps, as sensors have been replaced.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5428
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5428
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5428
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5428
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5428
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes