## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Lynwood House
34 Duham Road
Lanchester
DH7 0LS
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5469
DATE OF REPORT: 16/12/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5469
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Lynwood House
34 Duham Road
Lanchester
DH7 0LS
Carried Out On | 14/01/2021 17/12/2020, 13/01/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 31.01.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5469
SECTION 3: Report
LPC 17.12.20 1300 - 1610 Arrived on site and gained access to plantroom area . Foynd the condensate line from the flue header , to be snapped and condensate and products in to the area . The pipe work from the flue was not trapped , and just a 11/4 elbow pushed on to to the connection. Also found that the 2 x Remeha heating condensate lines , did not have traps fitted . Fitted non-mechanical traps to both of the heating boiler. Installed new condensate line from the common flue with a sealed connection on to the condensate thread. Formed a non mechanical trap as req . The 2 x water heaters on site have their own manufactuer condensate traps fitted . All 4 x appliances are connected to the common flue , so large amount of condensate being produced. NOTE ..... GAS APPLIANCES AND GAS PIPE WORK HAVE BEEN WORKED ON OR TESTED TODAY. Dave Hunter aware of work taken place today . If this work had not been done today the site would have been classed as IMMEDIATELY DANGEROUS. LPC 13.1.21 1510 - 1550 Identified correct gas meter as req. No gas appliances or pipe work worked on or tested tonight . LPC 14.1.21 0835 - Attended site and carried out commercial gas tightness test as per the guidance published in UP1A. The gas meter is located in the rear garden , that can be seen from the main road . There are actually 2 x external gas meters in the garden area . The one to the LHS ( smaller one ) is for the attached NHS building , whilst Lynwood House is the one on the RHS. Please note I have not worked on or tested the gas meter , pipe work etc to the NHS side . The gas meter meter is in a purpose built plastic housing . Both the ECV & AECV operate smoothly with labels of operation attached . The gas transporters warning advice notice is present and completed . The majority of the gas pipe work is run beneath ground level . There is a line diagram attached to gas meter , I can only assume that this is correct. The gas pipe work is earthed within the plantroom area, and sleeved through the wall . IVP - 0.405 m3 IVF - 0.0405 m3 IVP - 0.100 m3 Total - 0.5455 m3 S.O.S the plantroom > 60 m3 MAPD - 3.2 mb Let by - 3 minutes Stabilisation - 6 minutes TTP - 4 minutes Result .... Pass , zero drop detected or recorded with appliances connected. Whilst on site carried out commercial annual gas saftey , on 2 x AO Smith water heaters and 2 x Remeha Boilers. Every appliance is open flue (B23) and are connected to the same shared flue system . Each appliance has been tested as per manufacturers instructions, with all 26.9checks also. The burners have been removed from the 2 x boilers , but not from the 2 x water heaters ( Gaskets would be req ) Boilet no.1 LHS as been found to be IMMEDIATELY DANGEROUS , due to cracked combustion chamber cover and rotted bolts . As the cracked combustion cover has allowed POCS to escape , over time this has literally burnt through and rotted from bolts . Every attempt had been made to make the appliance safe , as gas supply cannot be capped off . Gas valve , Fan and ignition disconnected gas supply off at ECV and zip tie through the power supply . As the appliance is on a common flue , the combustion chamber has been sealed with silicone in the damaged areas. This has been done as a safe measure as is installing a Co detector above the appliance . Warning notice issued and label attached . Combustion and cooling ventilation is supplied via 2 x metal Louvred door , both communicate directly to outside. Does have measured and provide more than adequate ventilation to the area. As mentioned earlier all appliances are connected to a common flue header . Flue is well supported along its route, with a large non mechanical trap fitted. The flue torrents on the 2 x boilers also have condensate points , that are again both trapped and non mechanical. The Flue then enters a brick built chimney area , that runs vertically. I cannot guantee if the chimney is lined or not , nor can I guantee its route . The flue terminal can be clearly seen , from the rear of the building ( main road side ) There is an emergency stop button fitted to the LHS of the plantroom door , when pressed the gas supply is isolated to the area via a solenoid valve. The interlock controls are auto resetting and not manual , this is an existing installation. Gas pipe work is fully identified and well supported along its route to the appliances . Purge and test points are fitted and each appliance has it's own ECV. Appliance details Boiler 1 LHS Remeha Quinta pro 65 Sn , 1328307774870 Not tested as found to be ID - made safe . Boiler 2 RHS Remeha Quinta pro 65 Sn , 1328307774880 GFA High fire 02 , 5.1 Co2 , 9.0 Co , 35 ppm Ratio , 0.0003 Low fire 02 , 5.4 Co2 , 8.8 Co , 23 ppm Ratio , 0.0002 Water heater 1 LHS AO Smith BFC 80 G Sn , 134305174901002 GFA High fire 02 , 4.9 Co2 , 9.1 Co , 14 ppm Ratio 0.00001 Low fire 02 , 5.0 Co2 , 9.1 Co , 0 ppm Ratio , 0.0000 Water heater 2 RHS AO Smith BFC 80 G Sn , 134305174901001 GFA High fire 02 , 5.0 Co2 , 9.0 Co , 19 ppm Ratio , 0.0002 Low fire 02 , 5.1 Co2 , 8.9 Co , 0 ppm Ratio , 0.0000

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5469
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5469
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5469
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5469
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5469
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes