## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Stanley Court
Stanley
County Durham
DH9 6HD
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5470
DATE OF REPORT: 09/12/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5470
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Stanley Court
Stanley
County Durham
DH9 6HD
Carried Out On | 14/12/2020, 11/01/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 31.01.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5470
SECTION 3: Report
LPC 14.12.20 0940 - 1455 Attended site and carried out commercial gas tightness test as per the guidance published in UP1A. Traced pipework along its entire route , to allow calculation of total volume . The gas meter ( U40) is located the cleaners cupboard area , the door is marked up as GF10. The key for the door is located in the main key safe in the entrance area , I have attached a key ring that reads GAS METER ACCESS KEY GF10. The gas transporters ECV is an old Donkin wheel head valve , that isolates in reverse ( anti clockwise ) there is a label attached advising this . The valve is free moving and is not letting by as tested . There is an AECV fitted on the outlet side of the meter , again free moving with label of operation present . The gas transporters warning advice label is present , the pipe work is earthed / bonded Cleaners cupboard is not ventilated to outside . The gas pipe work leaves the meter in steel , runs under the suspended floor , then up through an unventilated duct. Enters the plantroom area at low level via the concrete floor unsleeved . Gas pipe work within plantroom is identified and supported along its route, test and purge points fitted . IVP - 0.108 m3 IVP - 0.0108 m3 IMV - 0.067 m3 Total - 0.1858 m3 S.O.P - 45 m3 - the cleaners cupboard area MAPD - 3 mb Let by - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result . Pass , zero drop recorded or detected with appliances connected. Warning notice issued, pipe work ran in unventilated ducts AT RISK. Carried out annual gas saftey inspection on 2 x open flue remeha boilers and 2 x room sealed water heaters. Each appliance has been tested for safe operation as per manufacturers instructions, with 26.9 checks carried out alongside. There is an old unused Remeha water heater still in situ , not connected to gas supply or to the DHW circuit . Burners have not been removed for inspection , due to seals being req . There are 2 x large metal vents in the wall , both at 3/4 wall height . Both vents communicate directly to outside, both have micro gauze fly screens fitted. The fly screens can easily become blocked, and restrict air for combustion and cooling purposes . As both vents are installed at the same height as watch other , high and low ventilation is not achieved as per BS6644 and manufacturers instructions. Ventilation does not seem to be having an adverse affect , on the 2 x open flue / B23 boilers. There is an emergency stop button at the plantroom door , when pressed the gas supply is isolated to the area , via a solenoid valve . The controls are auto resetting and not manual , this is an existing installation. The emergency stop button should have been upgraded to manual reset , when the water heaters got installed . Both of the Remeha Gas 210 boilers have have their heat exchangers , split and resealed with red sealant . I do not and cannot guantee if the correct materials have been used , nor do I know it's life expectancy. When repair like this are carried out , they are only a temp fix and not a permanent solution . The rest of the appliance components are all showing their age also . The fan can be heard to be fluctuating on the RHS boiler , its possible this will fail soon . Each individual appliance has it's own vertical flue fitted , that all enter an un-accessable room space . Inspection hatches are not fitted to allow visual inspection. The flue terminals can be seen clearly from the rear garden area. Flues do not have fire stops fitted as they penetrate the ceiling. Appliance details Boiler 1 RHS - open flue / B23 Remeha Gas 210 eco - 160 Sn , 0629101934420 GFA HIGH FIRE 02 , 5.4 Co2 , 8.8 Co , 31 ppm Ratio , 0.0004 LOW FIRE 02 , 5.3 C02 , 8.9 Co , 35 ppm Ratio , 0.0004 Boiler 2 LHS - open flue /B23 Remeha Gas 210 eco - 160 Sn , 0628401889410 GFA HIGH FIRE 02 , 5.4 Co2 , 8.8 Co , 30 ppm Ratio , 0.0003 LOW FIRE 02 , 5.0 Co2 , 9.0 Co , 48 ppm Ratio , 0.0005 Water heater 1 LHS Rinnai REU - KBM3237 HD LOW NOX Sn ,18.04 000020 Burner pressure Low fire - 1.2 mb High fire - 7.6 mb Water heater 2 RHS Rinnai REU - KBM3237 HD LOW NOX Sn , 18.04 000024 Burner pressure Low fire - 1.2 mb High fire - 7.6 mb Warning notice issued ..... Fly screens fitted to ventilation Ventilation not in the correct format / configuration No access to flues in ceiling void Controls not upgraded AT RISK.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5470
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5470
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5470
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5470
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5470
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes