## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Towneley Court
Stanley
County Durham
DH9 7NL
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5471
DATE OF REPORT: 02/02/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5471
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Towneley Court
Stanley
County Durham
DH9 7NL
Carried Out On | 01/02/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 06.02.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5471
SECTION 3: Report
LPC 1.2.21 0835 - 1615 Attended site and carried out annual gas saftey inspection, on the 2 x open flue boilers with Nuway burners fitted . The boilers themselves are Hamworthy Broadstones , size / capacity unknown . The burners have a range rating from 41 kw up to 133 kw . I do not know how these burners have been set up / rated at , as there isn't any commissioning reports or labels present . I have to assume worst case scenario that the burners have been set up at their max rating = 133 KW. Combustion ventilation calculation will be work out as boiler being 133 kw each . I have tested the burners for safe operation and achieved the GFA , as published in the manufacturers instructions. All 26.9 checks carried out as req . The boilers themselves are in really poor condition, no data badges present etc. Signs of corrosion to the rear flue connection , and the flues them selves . There are Asbestos stickers all over the plantroom, I cannot identify the actual model / version of broadstone boiler . I have to assume that the rear rope seals contain Asbestos , cannot and have not been touched . Burners have not removed , Boilers have not been opened either. Combustion ventilation is supplied via a large wooden square frame , in the wall with glass slats on an angle acting as louvers . The vent does not have a true high and low definition, the vent communicates directly to outside . The bottom piece of glass is missing so is wide open , snow , wind , rain and even vermin can easily enter the area . I have calculated the ventilation currently installed , I have found to more than adequate. But however this does comply with BS6644 . The rear area of the boilers that connects to the flue is badly corroded and damage to Gaskets , as are the flue themselves . These have been found to AT RISK and warning notice has been issued . I have tested around the rear of the appliances and the Gaskets , and did not detect any spillage at this time of testing . Co detector has been installed as a safe measure. Flue terminals can be clearly seen from the rear of the building . The gas supply enters the plantroom area at high level , and is sleeved through the wall . There is not an ECV installed for localised isolation purposes. Pipe work is earthed within the plantroom , but not at the point of entry. The pipe work is identified and partly supported, along its route to the boilers. There is a gas solenoid valve fitted at high level , but not stop button present. I can only assume that the solenoid is interlocked with the fire alarm , I have not been able to test this saftey features. Each burner has it's own ECV fitted . Appliance details Boiler 1 LHS Hamworthy Broadstone Burner Nuway STG146/2 Sn , 2450582 GFA 02 , 3.4 Co2 , 10 Co , 35 ppm Ratio , 0.0003 Boiler 2 RHS Hamworthy Broadstone Burner STG146/2 Sn , 2498731 GFA 02 , 3.4 Co2 , 9.9 Co , 91 ppm Ratio 0.0009 In my honest opinion the 2 x boilers req replacing asap , and the 2 x burners could be reused with the new boilers . I do not believe that these 2 x burners have been fully set up / range rated accordingly to the building heat requirements. I highly recommend getting the burner manufacturer involved, to carry out a full commission and provide all the relevant paper work and Information on range setting . Carried out annual commercial gas tightness test as per the guidance published in UP1A. The gas meter is located at the rear of the building , in an unventilated wooden meter housing . The roof of the meter housing has completely collapsed , exposing the meter to the elements The wooden structure of the frame is also rotten . There is a wheel head type ECV fitted on the incoming main , the head itself is cracked and only half of it remains. This makes it very difficult to shut off the valve in an emergency situation . The valve has been reported to Northen Gas Networks - JOB ID NO , 736 21645. They have attended site and are returning tomorrow to fit a new head . Karbon housing have also been alerted , to carry out n emergency repair to meter housing . The gas transporters warning advice notice is not present , also the gas meter is not secure ,as the bracket is not fixed ot the wall . There is an AECV fitted to the outlet side of the meter , than operates smoothly. A short length of 2 " steel is fitted on the outlet side of the meter , then the gas supply is ran externally in track pipe. The pipe is coated in a plastic yellow for protection and identification purposes . The track pipe runs vertically up the rear of the building, clipped along its route . Then runs horizontal along the roof above , then finally makes a connection outside the plantroom . Traced gas pipe work along its entire route , then calculated the total volume as req IVP - 0.072 m3 IVF - 0.0072 m3 IMV - 0.067 m3 Total , 0.1462 m3 S.O.S - the plantroom - 35 m3 MAPD - 2.4 mb Let by - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result ..... Pass , zero drop recorded or detected with appliances connected. Warning notice issued, for head on GAS ECV half missing , meter house collapsing AT RISK

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5471
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5471
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5471
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5471
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5471
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes