## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Unit 2D
The Waterfront
Goldcrest Way
NE15 8NZ
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5473
DATE OF REPORT: 12/01/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5473
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Unit 2D
The Waterfront
Goldcrest Way
NE15 8NZ
Carried Out On | 15/01/2021, 18/01/2021, 19/01/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 23.01.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5473
SECTION 3: Report
LP + DA 15.1.21 0830 - 1430 Attended site and carried out commercial gas tightness test as per the guidance published in UP1A. Traced gas pipe work along its entire route, found pipe work to run in boxing that is open at both ends. The majority of pipe work runs via the suspended ceilings, pipe work is partly identified but well supported along its route . The gas meter is located in a ventilated cupboard within Propery Admin office . Cupboard door is kept unlocked at all times , for full time access . The gas transporters warning advice label is present . I have reccomend that site contact northern gas networks , as the main ECV is on the stiff side to operate . The AEC is smooth to operate , with operation diagram on the handle . As gas pipe leaves and breaks through to another floor level above , fire stops are fitted. I unable to confirm if pipe work is sleeved through floors/ walls due to fire protection fitted. Each appliance has it's own ECV fitted , purge and test points also present. I have attached a gas approved label to gas meter cupboard door , that reads " ENERGENCY CONTROL VALVE LOCATED IN THIS CUPBOARD " There is also a gas test rig installed in the main warehouse area , this is used to train Karbons own gas engineers . I have tested up to the ECV that isolates the test rigs U6 gas meter . After the ECV there is a solenoid valve fitted , again not tested. This gas line and the appliances have not been tested, as these are out of scope of the gas regs , as this is an educational training area / facility . ( carried out localised tightness test on test rig as per UP1B , found to be gas tight with appliances connected ) IVP - 0.2404 m3 IVF - 0.02404 m3 IMV - 0.067 m3 Total - 0.33144 m3 S.O.S - Office - 28 mb MAPD - 2.8 mb Let by - 2 minutes Stabilisation - 6 minutes TTP - 3 minutes Result ... Pass , zero drop recorded or detected with appliances connected. Waited until 1430 for scaffold, but it never arrived . Informed Dave Aston , who is going to cancel delivery for today . LPC / DA 18.1.21 0825 - 1055 See Dave Astons full report Onsite 0800 -1050 Da onsite 0800 1050 Scafolding not delivered until 0945 and found to be wrong hss unable to deliver more scaffolding so after phone calls leave site 1050 LPC 19.1.21 0820 - 1300 Called to suppliers and collected saftey harness etc , then proceeded to site . Arrived at job and gained access to area , tested and familiarised myself with the access equipment hired . There are a total of 5 x suspended heaters installed in the warehouse area, 3 x radiant tube heaters and 2 x air heaters . 2 x ( no 5 & 4 ) of the Bensen air heater have been found to isolated as their gas ECVS are in the off position , with an AT RISK Label fitted ( was not visable from below ) I have attached a new Warning label, and left isolated as found . Heater no.3 that is an Ambirad radiant tube heater , has had the gas supply capped off and the flue removed . So not in use, but still in situ . Heaters 1 & 2 are again Ambirad tube heaters , that are still connected to the gas supply and still in use . I have spoken to manufacturers today regarding heaters 1 & 2 and their ventilation requirements . According to manufacturers instructions ( page 16 ) , air changes can be taken into consideration, as long as minimum combustion ventilation is present as stated in the manual. There is not any combustion ventilation installed at all within this area. It is clear to see that the building has been heavily modified, as offices have been built . There is combustion ventilation in the wall at high and levels , but this now encompassed within the office area . To the extent that there is still a radiant tube heater still present above the suspended ceiling, above the top floor office area . The gas supply is capped off to it as not in use , flue in still connected . See image as attached . As the heaters 1 & 2 are not installed to manufacturers instructions, these are both AT RISK. Gad supply and electrical supplys isolated , warning labels attached with warning notice issued . There is also a Worcester combi boiler installed in the same area, this supplys CH & DHW to the Site . This has been tested for safe operation as per manufacturers instructions , found GFA readings to with tolerance . The probes has been replaced with the upgraded items . Appliance Details Worcester Greenstar 42 CDI Sn , 3730 304 006051 7713331019 GFA High fire 02 , 3.4 Co2 , 10 Co ,46 ppm Ratio, 0.0004 Low fire 02 , 5.1 Co2, 9.0 Co ,17 ppm Ratio , 0.0001 Air heaters / tube heaters No.1 Warehouse Ambirad AR35UTGB Sn , 060311738819 AT RISK isolated No.2 Warehouse Ambirad AR35UTGB Sn , 060311733820 AT RISK isolated No.3 Warehouse Ambirad AR35UTGB Sn , 060311733825 NOT IN USE GAS SUPPLY CAPPED , FLUE REMOVED No.4 Warehouse Benson- air heater Varinate 2 RS Sn , 413536 Found gas and electric supply isolated AT RISK label attached , LEFT AS FOUND - NOT IN USE No.5 Warehouse Benson - air heater Varinate 2 RS Sn , 413537 Found isolate gas and electric supply isolated AT RISK label attached , LEFT AS FOUND - NOT IN USE No.6 In ceiling void above top floor office Ambirad AR35UTGB Sn , 060311733810 FOUND GAS SUPPLY CAPPED OFF AND MADE SAFE NOT IN USE .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5473
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5473
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5473
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5473
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5473
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes