## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
The Manors
Adderlane Road
West Wylam
NE42 5ET
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5487
DATE OF REPORT: 19/01/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5487
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | The Manors
Adderlane Road
West Wylam
NE42 5ET
Carried Out On | 04/02/2021, 08/02/2021 09/02/2021, 16/02/2021, 23/02/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 16.02.2021 Catering Gas Check for temporary catering facilities

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5487
SECTION 3: Report
LPC 4.2.21 0830 - 1130 Attended site to carry out annual commercial gas tightness test as per the guidance published in UP1A. The gas meter is a boundary meter , located in a plastic purpose built housing . Up on approach to the gas meter , I could clearly smell gas. I used LDF and a gas sniffer as checked / tested around the meter . I found gas leak to be on the gas transporters side , on the thread on the Govenour . When sprayed with LDF a large leak is clearly present . I called Transco 0800 111 999 and reported the issue on site . The adviser stated to isolate gas supply via the ECV , so I made safe as instructed . I have isolated the appliances via the control panel as in the off position , also interlock isolated to kitchen area. AECV on outlet side of the meter turned off , to keep the gas line pressurised. Northen gas emergency services / Transco attended site , and confirmed the leak and issued a warning notice . The Engineer has notified the gas supplier , who has spoken to Mark the Manager on site . Warning notice has been issued by Northen gas and recieved by Mark theManager on site . Photo taken off warning notice issued NORTHEN GAS NETWORKS / Transco JOB REF NO - 5362 7209 NO GAS APPIANCES OR GAS PIPE WORK TESTED OR WORKED ON TODAY. LPC 8.2.21 0855 - 1620 Attendend site and carried out commercial gas tightness test as per the guidance published in UP1A. The gas meter ( boundary meter is located in a purpose build plastic housing , with ventilation and a lockable door. The meter housing is situated in the front garden area , I front of the car park . Both the ECV and AECV at the gas meter are free moving , complete with labels of operation . The gas transporters warning advice notice is also present at the meter . The majority of the gas pipe work is ran below ground level , a line drawing is not present . I can only assume that the pipe work has been ran , in the straightest and shortest route possible . The gas pipe work enters the plantroom area at low level , with an ECV upon entry for localised isolation purposes. Pipe work tees off to supply the 4 x Remeha boilers installed . The pipe work then continues at ceiling height , leaves the plantroom passes through the laundry, finally terminates at the kitchen area. Pipe work is fully identified within the plantroom , pipe work to the kitchen is identified every metre . Pipe work is well supported throughout it different routes. The kitchen has it's own solenoid valve and a ECV both situated in the plantroom area. There is also a main solenoid valve fitted just past point of pipe work entry . There is an emergency stop button at the plantroom door , when pressed the gas supply is isolated to the building . The interlock controls within the plantroom are auto resetting, and not manual this is an existing installation. The gas pipe work passes through the laundry room and high level and is boxed in . Also not sleeved through wall . Gas pipe work is earthed within plantroom area, not at the meter . The boxing does not have ventilation installed , this AT RISK and a warning notice has been issued . IVP - 0.144 m3 IVF - 0.0144 m3 IMV - 0.067 m3 Total - 0.2254 m3 S.O.S - the laundry - 30 m3 MAPD - 2 mb Let by - 2 minutes Stabilisation - 2 minutes TTP - 2 minutes Result.... Pass , zero drop recorded or detected with appliances connected. Carried out annual gas safety inspection on site , appliances tested as per manufacturers instructions. All 26.9 checks also carried out along side . The gas fired plant within the plantroom consists of 3 x Remeha quinta 115 and 1 x quinta 65 , all in poor condition All appliances are room sealed and all terminals are on the same wall at low level , this does not comply with the clean air act . The flue elbow seal is buried in the wall , due to the way the wall has been pointed up around the flue , the joint cannot be visually inspected. I have carried out an air quality test on the inlet side of the concentric flue , found to be ok . Installation AT RISK. Boiler no.4 RHS is a quinta 65 this is not running and has not been worked on or tested tested. There is an AT RISK label attached to the appliance , front case is cracked and flue severely damaged . Found boilers 1,2 and 3 to have serious condensate damage , as plastic all cracked , solenoid covers on gas valves split and drainage present . Found that the appliances at some had new internal plastic flues replaced . The flues had not been seated correctly into the sump connector , this allows products of combustion and condensate to escape . The internal flues from these boilers have been removed, sumps fully cleaned out , as heavily blocked . Install new sump gasket , lubricate the telescopic flue seals and finally refitted the flues . The burners have been removed for inspection , new gaskets and probe replaced as req . Found the gas connection on the gas valve to boiler no.2 , to be cross threaded. I attempted to repair it , but it will not seal . The top plastic hanger of the front casing has been damaged by the prolonged, exposure to condensate as it has been eaten away . As this is a room sealed appliance, this cannot be used like this . I have capped the gas supply off to the appliance , unable to test . Ventilation for cooling purposes is supplied via 2 x large wooden louverd doors . Both doors communicate directly to outside , and supply more than adequate ventilation for cooling purposes . Appliance details Boiler 1 Remeha Quinta 115 115 kw - not rated Sn , 0912406587610 GFA High fire 02 , 4.6 Co2 , 9.3 Co , 39 ppm Ratio , 0.0004 Low fire 02 , 4.5 Co2 , 9.3 Co , 9 ppm Ratio 0.0000 Boiler 2 Remeha Quinta 115 115 kw , not rated Sn , 0912406587600 NOT TESTED FUE TO GAS LEAK ON GAS VALVE. Boiler 3 Remeha Quinta 115 115 kw , not rated Sn ,0912406587590 GFA High fire 02 , 5.4 Co2 , 8.8 Co 36 ppm Ratio 0.0004 Low fire 02 , 4.8 Co2 , 9.1 Co , 15 ppm Ratio , 0.0001 Boiler 4 Remeha Quinta 65 65 kw , not rated Sn , 091380666620 NOT WORKED ON TESTED , AS NOT WORKING CATERING APPLIANCES NOT WORKED ON OR TESTED . LPC 16.2.21 0810 - 0930 Called to suppliers first and collected CP42 as req then proceeded to site . Gained access to building to , Gas appliances in kitchen in use , kitchen not been shut down for gas inspection. This had been arranged for today between Mark and Dave Aston . Informed both Dave's . NOT WORKED ON OR TESTED ANY GAS CATERING APPLIANCES OR WORKED ON GAS PIPE WORK TODAY. LPC 23.2.21 0830 - 1630 Attended site and Carried out annual commercial catering saftey inspection, as per guidance published in UP19. Each individual burner and associated controls have been tested for safe operation, as have the thermostats etc. The commercial gas catering equipment consists of , 1 x fan assisted range , 1 x twin burner fryer , 1 x solid top and 1 x high level grill . All appliances are in good condition , with the correct gas hoses , governors and restraints fitted . Each appliance has it's own ECV fitted to allow individual isolation , all bayonet fittings are installed correctly. Appliance details Fryer Blueseal GT46 SN , 440659 22.5 kw - not rated B.P - 9.8 mb Grill Blueseal G91B SN , 441355 8.8 kw - not rated B.P - 10 mb Range with convection fan Blueseal G56DF SN , 439011 46.8 kw - not rated B.P - 9.5 mb Solid top Blueseal G516 A B SN , 441788 16.5 kw - not rated B.P - 9.5 mb Found that govenour to be very unstable and burner pressure , very inconsistent - made safe hose removed new 3/4 govenour req . The copper manifold behind the appliance is well supported with brackets , each connection to the appliance is also secure to avoid pipe work being strained. Gas pipe work enters the area via high level and runs down through the canopy channel , ECV fitted for localised isolation purposes. Pipe work is partly identified, test and purge point present on the manifold . There is an Island canopy installed that has the correct overhang , with baffle filtration that is kept clean . The installation has mechanical extraction and ventilation installed . When either of these functions is turned off , the gas supply is isolated to the area . There is also 2 x engency stop buttons installed at both doors , when either is pressed again the gas supply is isolated to the area . The interlock control panel is is manually resetting , as UP19. The gas solenoid valve is located in the plantroom at high level , this is working ok as tested . When pipe work has been originally installed the flux has not been fully cleaned off , as green residue present around fittings. Tested working pressure with appliances running , found to be ok . The mechanical ventilation has closable fins fitted, also there is a filter installed externally on the air intake . I do not know if or when this filter was replaced or tested , as there is not a handman on site - this is AT RISK , as filter could become blocked and severely reduce air flow Carried out ambient co co2 test as per guidence published in UP19 , lit all burners and turned to max . Ventilation and extract in normal use position , as marked on dials . Shut all windows , doors and serving counter , allowed to run for twenty minutes . Carried out test and found that installation failed , as readings above permissible limits of 2800 ppm , but not above 5000 ppm . The installation is AT RISK and a warning notice has been issued , labels attached and supply left isolated via fuse spares . Site Manager has been made aware of issues. The ideal solution would to install a hard wired co2 monitoring device that is interlocked with the gas supply . The manufacturer of the existing panel can supply a plug and play monitor.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5487
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5487
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5487
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5487
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5487
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes