## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Weavers Court
Swordy Drive
Alnwick
NE66 1SZ
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5489
DATE OF REPORT: 26/02/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5489
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Weavers Court
Swordy Drive
Alnwick
NE66 1SZ
Carried Out On | 11/02/2021, 26/02/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
AGSC TD 11.03.2021 We req ....... (FOW EG asked DA what next steps are) 2 x fans - for boilers 1 & 2 Another combustion chamber cover for boiler no 3 Each boiler reqs a new burner Boilers are ..... Remeha Quinta pro 115

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5489
SECTION 3: Report
LPC 11 221 0930 - 1610 ( 70 miles to home ) Attended site and carried out annual commercial gas saftey inspection , on the 3 x Remeha boilers ( open flue B23) installed. I have tested the appliances for safe operation as per manufacturers instructions, with all 26.9 checks carried out . I have found the combustion chamber covers , on all 3 x appliances to be cracked and split. As I only have 2 x covers with me , boiler no.3 RHS has been found to IMMEDIATELY DANGEROUS and the gas supply has been capped off . As the boilers are connected to a common flue I have sealed up the splits on boiler no.3 , as a safe measure a Co detector has been installed . The other 2 x boilers have had new combustion chamber covers fitted , with Gaskets and probes as req . Heat ex and burners have been visually inspected. Found the burners to worn and req replacing , along with the fans that are noisy. Ventilation for combustion and cooling purposes is supplied via 4 x grills cut into the plantroom door , at high and low levels. The grills all communicate directly to outside, they have been measured and found to be more than adequate. All 3 x boilers are connected to a common flue header, then enters the wall within the plantroom . I do not know its route or if the material used is continuous, or if a liner is used . I have gained access to the main loft area and the flue is not visable to inspect . The flue visable within the plantroom area , has various signs of corrosion present, and areas that have has temp repairs carried out . I cannot see any condensate dripping from the flue at the moment . The condensate lines have been badley installed , a non mechanical trap is fitted . FLUE IS AT RISK DUE TO CORROSION AND REQS INTERNAL SEALS REPLACING, POSSIBLY MORE . The flue terminal is clearly visable from the front of the building . There is a boundary meter at the front of the building , tightness test has not been carried out . The gas supply enters the area at low level with an ECV and Solenoid valve fitted , upon entry with a secondary gas meter . There is also an emergency stop button installed , when pressed the gas supply is isolated to the area The controls are manually reset via a button on the control panel as req . Pipe work is fully identified and supported, with test and purge points fitted. Each appliance has it's own manufacturers ECV fitted . Appliance details Boiler 1 LHS Remeha Quinta pro 115 Sn , 1522211971310 115 kw not rated GFA High fire 02 , 4.9 Co2 , 9.1 Co , 53 ppm Ratio , 0.0006 Low fire 02 , 6.1 Co2 , 8.4 Co , 118 ppm Ratio , 0.0014 Boiler 2 Middle Remeha Quinta pro 115 Sn , 1517511716910 115 it not rated GFA High fire 02 , 4.7 Co2 , 9.2 Co , 67 ppm Ratio , 0.0007 Low fire 02 , 6.0 Co2 , 8.5 Co , 21 ppm Ratio , 0.0002 Boiler 3 Middle Remeha Quinta pro 115 Sn , 1522311977300 115 kw not rated NOT TESTED AS IMMEDIATELY DANGEROUS, GAS SUPPLY CAPPED OFF. 0 Attend site 26/02/21 to carry out a tightness test . Walk site and measure gas pipework . Only allowed to turn gas off at 1315 when kitchen not in use. G40 meter volume .100m3 Pipework volume .81m3 Total volume .91m3 Test Let by 4mins Stabilisation 6mins Tightness test 6mins Total 16mins 0mb drop kitchen not tested Lee to test when he carries out the catering check Offsite 1400

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5489
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5489
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5489
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5489
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5489
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes