## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Aldwych House
Commercial Road
South Shields
NE33 1UE
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5490
DATE OF REPORT: 03/03/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5490
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Aldwych House
Commercial Road
South Shields
NE33 1UE
Carried Out On | 02/03/2021, 03/03/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 18.03.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5490
SECTION 3: Report
LP 2.3.21 0830 - 1300 Arrived on site and gained access to plantroom, after finally locating keys as another contractor had them . Found that only 2 x boilers are actually running , out of the 4 x fitted ( no 1 & 2 not running) The first stage actuators in the flue dampers are seized solid, left isolated as actuators will req replacing . Only worked on boilers 3 & 4 , called off site to attend callouts as per office . Boiler 3 Hamworthy Purewell classic 70 Auto 70 kw not rated Sn , SG04A1HGB31060 Burner pressure Low - 2 mb High - 11 mb GFA Low fire 02 , 10.5 Co2 , 5.9 Co , 0 ppm Ratio , 0.0000 High fire 02 , 6.2 Co2 , 8.4 Co , 11 ppm Ratio , 0.0001 Boiler 4 Hamworthy Purewell classic Auto70 70 kw not rated Sn , SG04A1HGB31057 Burner pressure Low - 2 mb High - 11 mb GFA Low fire 02 ,9.4 Co2 , 6.6 Co , 1 ppm Ratio , 0.0000 High fire 02 , 6.5 Co2 , 8.1 Co , 0 ppm Ratio , 0.0000 Gas pipe work has not been worked on or tested today . PPM task not complete . LPC 3.3.21 0820 - 1230 Attended site and carried out annual commercial gas tightness test as per the guidance published in UP1A. The gas meter is located in the plantroom , next to the plantroom door . The area is well ventilated via 2 x large louverd doors, that both communicate directly to outside. Gas transporters/ suppliers warning advice notice is posted on the wall above the meter . Both the ECV and AECV are smooth operating, complete with labels of operation. Earth bonding present at the meter . Gas pipe work is fully identified and well supported along its route to the boilers . Each appliance has it's own fitted , purge and test points also present . There is an emergency stop button at the plantroom, when pressed the gas supply is isolated to the area via a solenoid valve. The controls req to reset manually , this is correct and working ok as tested . IVP - 0.0192 m3 IVF - 0.00192 m3 IVF - 0.067 m3 Total - 0.08812 m3 S.O.S the plantroom > 60 m3 MAPD - 4.2 mb Letby - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result.... Pass , zero drop recorded or detected with appliances connected. Whilst on site carried out annual gas saftey inspection , appliances have been tested for safe operation as per manufacturers instructions ( boilers 1 + 2 not running ) Combustion ventilation is supplied via 2 x large wooden Louvred doors , both doors communicate directley to outside. The ventilation installed is more than adequate for combustion and cooling purposes as measured and calculated. All 4 x boilers are connected to a common flue system , that is suspended from the ceiling from rods. The flue has dampers fitted that are locked in the fully open position, as each boiler has it's own mechanical flue damper fitted . The flue seems to be in fair condition, with no obvious signs of corrosion present . The enters a brick built chimney, I do not know if the chimney is lined or the. I have carried out flue flow and spillage tests , and found the flue to be operating ok . As mentioned earlier in this report the gas meter is located in the plantroom. Found gas interlock controls ( emergency stop button , gas solenoid and rest button ) to be working ok as tested . Appliance details Boiler 1 Hamworthy Purewell classics Auto 70 70 kw not rated Sn , SG04A1HGB31066 NOT TESTED AS PARTS REQ Boiler 2 Hamworthy Purewell classic Auto 70 70 kw not rated Sn , SG04A1HGB31067 Boiler 3 Hamworthy Purewell classic 70 Auto 70 kw not rated Sn , SG04A1HGB31060 Burner pressure Low - 2 mb High - 11 mb GFA Low fire 02 , 10.5 Co2 , 5.9 Co , 0 ppm Ratio , 0.0000 High fire 02 , 6.2 Co2 , 8.4 Co , 11 ppm Ratio , 0.0001 Boiler 4 Hamworthy Purewell classic Auto70 70 kw not rated Sn , SG04A1HGB31057 Burner pressure Low - 2 mb High - 11 mb GFA Low fire 02 ,9.4 Co2 , 6.6 Co , 1 ppm Ratio , 0.0000 High fire 02 , 6.5 Co2 , 8.1 Co , 0 ppm Ratio , 0.0000 The general condition of the associated plant and controls is poor , due to age and usage . Various actuators have been removed from their valve bodys. Warning notice issued Chemicals and Combustable items present in plantroom .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5490
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5490
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5490
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5490
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5490
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes