## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Matfen Court
Chester-Le-Street
County Durham
DH2 2TX
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5491
DATE OF REPORT: 16/02/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5491
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Matfen Court
Chester-Le-Street
County Durham
DH2 2TX
Carried Out On | 15/02/2021 16/02/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 19.03.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5491
SECTION 3: Report
LPC 15.2.21 0815 - 0850 Attended site and called off to attend an emergency on another site. Gas appliance or pipe work have not been tested or worked on today . LPC 16.2.21 10:00 - 1630 Attendee site and carried out commercial gas tightness test as per the guidance published in UP1A. Traced gas pipe work along its entire route , then calculated the volume . The Gas meter is located in a brick out building next to the plantroom, at the rear of the building . The out building has a metal door with a grills at high level , the key is clearly labelled in the main safe . The Gas transporters warning advice label is posted behind the meter . The ECV does not operate smoothly and has the wrong handle fitted , that keeps falling off when used . The ECV is also very difficult to use , as operation does match with the label of operation sticker attached . The pipe work then passes through the wall into the plantroom , not sleeved through the wall. Pipe work is earth bonded within the plantroom, above the secondary meter installed in the plantroom . Pipe work is fully identified and supported along its route to the boilers . Each boiler has it's own ECV fitted to it . I have rang 0800 111 999 and reported the issue regarding the operation of the ECV , their ref no - 536 43282 IVP - 0.061 m3 IVF - 0.0061 m3 IVM - 0.100 m3 Total - 0.1671 m3 S.O.S - the plantroom - 45 m3 MAPD - 3 mb Let by - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result..... Pass , zero drop recorded or detected with appliances connected. WARNING NOTICE ISSUED AS AT RISK . Whilst on site carried out annual gas saftey inspection , on the 2 x open flue ( B23)Remeha boilers installed . Boiler appliances have had their burners removed inspected , heat ex inspected and cleaned . Gaskets and probes have been replaced as per the service kit supplied . Each boiler has been tested for safe operation as per manufacturers instructions, with all 26.9 checks also carried out . Combustion ventilation is supplied via 2 large metal louverd doors , both doors communicate directley to outside . The doors do not have a true high and low level definition. Both doors have micro gauze fly screens fitted, this cam easily become blocked . The fly screens do not comply with BS6644 and are AT RISK - warning notice has been issued. The doors do supply more than adequate ventilation for combustion and cooling purposes, as measured and calculated. There is an emergency stop button fitted at the plantroom door. When the button is pressed the gas supply is isolated to the area , via solenoid valve . The controls are auto resetting and not manual , this is an existing installation. Both boilers have their own prima + flues fitted , that are suspended from the ceiling , each joint has bands fitted . Both flues then enter a brick built chimney, both flues are ran inside un used twin wall flue pipe. Both have condensate lines, that are tee'd together with a non mechanical trap fitted. Both flues have various signs of corrosion present ( particularly in the chimney area ) and ideally req a flue specialist to attend site . Found flue from boiler no1 LHS to be leaking really badley within the chimney , access is very poor. The seal is clearly visable as the joint has not been made properly , severe staing beneath flue joint . Gas supply to boiler no.1 has been capped off as IMMEDIATELY DANGEROUS. I have carried out an ambient co/co2 test around the boiler 2 flue with it running, I didnt detect any products of combustion present at this time of testing . There is signs of temporary repairs present. A co detector has installed as a safe measure , warning notice issued AT RISK. The flues reduce in their diameter as they enters the chimney , I do not know if this is correct or not. Both appliances are operating safely and correctly, I can only assume that the flues have been designed accordingly. Both flue terminals can be clearly seen from below . To enable boiler no.1 LHS to be tested a new control interface PCB has been fitted today . Appliance details Boiler 1 LHS Remeha Quinta pro 115 115 kw not rated Sn , 1025700508210 GFA High fire 02 , 4.9 Co2 , 9.1 Co , 56 ppm Ratio 0.0006 Low fire 02 , 6.0 Co2 , 8.5 Co , 7 ppm Ratio , 0.0001 GAS SUPPLY CAPPED AS IMMEDIATELY DANGEROUS Boiler 2 RHS Remeha Quinta pro 115 115 kw not rated Sn , 1025700506650 GFA High fire 02 , 4.7 Co2 , 9.2 Co , 62 ppm Ratio , 0.0007 Low fire 02 , 6.0 Co2 , 8.5 Co , 10 ppm Ratio , 0.0001

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5491
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5491
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5491
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5491
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5491
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes