## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Unity Hall
71 Mill Dam
South Shields
NE33 1EQ
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5492
DATE OF REPORT: 21/02/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5492
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Unity Hall
71 Mill Dam
South Shields
NE33 1EQ
Carried Out On | 08/03/2021, 11/03/2021, 19/03/2021, 26/03/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
AGSC TD 19.03.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5492
SECTION 3: Report
LPC - CS 11.3.21 0840 - 1630 Arrived on site and gained access to basement plantroom. Found that boilers are taking their combustion air from the cavity . Also there is a flue liner ran within the cavity , upon close examination the complex has rotted through. The stainless flue internally is also rotten and has been patched up with tape . There are non recognise fittings used on the condensate line . There front boiler casings have failed as the plastic has been damaged by heat and condensate . The plastic internal flues and seals have failed within the boilers, allowing products of combustion to escape. Both appliances have been found to be IMMEDIATELY DANGEROUS, gas supply to both boilers has been capped off to make safe . DHW calorifiors have immersion fitted that are working, so site will have DHW. Temporary heaters have been collected from local suppliers , to be supplied to Tennents as req John the flue specialist has attended site and has designed a new flue system to be installed . Converting the appliances back to standard room sealed configeration , using a concentric flue system. Temp heaters have been issued to Tennents. Assist Dave Hunter to get heating back on. 1530 -1830 26/03/21 0900 attend site to carrybout ppm service

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5492
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5492
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5492
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5492
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5492
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes