## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
162 Albert Road
Jarrow
Tyne & Wear
NE32 5RR
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5494
DATE OF REPORT: 09/03/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5494
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | 162 Albert Road
Jarrow
Tyne & Wear
NE32 5RR
Carried Out On | 05/03/2021 09/03/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 24.03.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5494
SECTION 3: Report
LPC 5.3.21 1230 - 1355 Attempted to gain access with keys supplied , but keys incorrect. Found that a key safe had been installed in rear yard , attempted to gain access again , but key snapped in lock barrel as seized solid. Phoned Janet from Karbon , but unable to get a joiner over today to allow access . Dave Hunter aware . LPC - CS 9.3.21 0945 - 1610 Attended site and carried out commercial gas tightness test as per the guidance published in UP1A. The gas meter ( U16) is located in a ventilated cupboard , in the main entrance hallway. The ECV is free moving with label of operation attached . Gas transporters warning advice label is posted above the gas meter . Earth bonding present at gas meter , gas pipe work is identified where visable . Gas pipe (42 mm copper )work leaves the meter and runs beneath the suspended floor , finally breaking through in the plantroom ( at the rear of the building ) I can only assume the pipe work run , as a line drawing is not present . Gas pipe work has been sealed near the meter , and is not ventilated along its run . This is AT RISK and a warning notice has been issued . The gas pipe work within the plantroom is , well supported and fully identified. ECV fitted upon entry for localised isolation purposes, purge and test points also present . IVP - 0.0144 m3 IVF - 0.00144 m3 IMV - 0.025 m3 Total - 0.04084 m3 SOS - the plantroom - 25 m3 MAPD - 1.7 mb Letby - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result ..... Pass , zero drop detected or recorded with appliances connected. Whilst on site carried out annual commercial gas saftey inspection , on 2 x Ideal Evomax boilers . Both boilers have tested for safe operation as per manufacturers instructions , with all 26.9 checks carried out along side. The plantroom is located at the rear of the building , and is accessed via the back gate . Both boilers have flue ploom diverter kits fitted , that are situated below an opentable window. Terminals are more than 300mm away from the stair well window . Flues are in good physical condition, no signs of damage or vandalism present at time visit. Ventilation for cooling purposes only as both boilers are room sealed , is supplied via a large wooden louverd door. The door communicates directly to outside , and supplies more than enough ventilation as measured and calculated. There is an emergency stop button fitted at the plantroom door , when pressed the gas supply is isolated to the area. There is a Merlin GDP2 interlock installed in the plantroom , with a hard wired methane detector fitted . The panel also has a stop button built , gain when pressed the gas supply is isolated to the area . The interlock controls are req to be manually reset and not auto. This is working ok as tested . I have not be able to test the methane detector as I do not have the correct gases . The correct test gases are available from the manufacturer S&S . Appliance details Boiler 1 LHS Ideal Evomax 40 40 kw not rated Sn , ACK 20595800002918 GFA High fire 02 , 4.5 Co2 , 9.3 Co , 81 ppm Ratio , 0.0009 Low fire O2 , 5.3 Co2 , 8.9 Co , 25 ppm Ratio , 0.0003 Boiler 2 RHS Ideal Evomax 40 40 kw not rated Sn , ACK 20595800002909 GFA High fire 02 , 4.3 Co2 , 9.4 Co , 99 ppm Ratio , 0.0010 Low fire 02 , 5.7 Co2 , 8.7 Co , 20 ppm Ratio , 0.0002 Pressurisation unit is interlocked to the controls , to prevent dry firing / running .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5494
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5494
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5494
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5494
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5494
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes