## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Rooms within House, Abbott House
1 Quarry Bank Court
Elswick
NE4 6NG
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5495
DATE OF REPORT: 10/03/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5495
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Rooms within House, Abbott House
1 Quarry Bank Court
Elswick
NE4 6NG
Carried Out On | 10/03/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 24.03.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5495
SECTION 3: Report
LPC - CS 10.3.21 0835 - 1630 Arrived on site and gained access to plantroom . Worked out combustion ventilation, found to have fly screen that are completely blocked . Removed and cleaned , but found to be undersized. Carried out visual inspection of flue dilution system , found to all joints to be tapped up and loose . When tape was removed and exposed terrible condition of flue . Found installation to be IMMEDIATELY DANGEROUS and capped off gas supply to appliances . Waited for Jim park to arrive from Karbon housing to visual inspect along side. Jim agreed that site is ID , temp heaters have been delivered to site . New plantroom to be installed as appliances etc , beyond economical repair . Paper warning notice issued as IMMEDIATELY DANGEROUS , gas supply capped off , no CH or DHW to site

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5495
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5495
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5495
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5495
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5495
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes