## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Holmewood House
13 Esplanade West
Sunderland
SR2 7BG
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5498
DATE OF REPORT: 25/03/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5498
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Holmewood House
13 Esplanade West
Sunderland
SR2 7BG
Carried Out On | 22/03/2021, 25/03/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 31.03.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5498
SECTION 3: Report
LPC - CS 22 .3.21 0820 - 1630 Attended site and carried out annual commercial gas tightness test as per the guidance published in UP1A. The gas meter is located in a cupboard, beneath the front door stairwell . The cupboard wooden door is behind a locked gate , the key is identified as " gas cupboard key " Staff are all aware of the gas meter location. The door has holes drilled at high and low levels , to provide ventilation. The gas transporters govenour on the meter is showing significant signs of corrosion . Also the gas transporters ECV is letting by , as detected on the letby test . Northern Gas Networks have been contacted and informed , their job reference no - 5367 - 8299 . There are 7 x individual domestic gas boilers installed , off one large supply . There are 8 x individual gas supplys entering the building ( only 7 x boilers ) After many hours of searching finally found a capped off gas supply and redundant fuse spare , in the other down stairs toilet area ( confirming that there was originally another boiler present = 8 in total . Each individual gas supply runs externally up the front of the building . Each line has it's own individual ECV and test point , but the lines are not identified to state what flat / area they supply . Pipe work is showing significant signs of corrosion and is pitted , but not leaking at this time of testing . Pipe work is partly identified externally, but not at all internally where visable . Traced gas pipe work internally as best as possible, as majority ran beneath floor board and in false walls . Also gas pipe work ran in various unventilated ducts , and non gas family ECVS fitted . Gas transporters warning advice label is present at the gas meter and is completed. Both the ECV & AECV are smooth operating with labels of operation present . Each of the 6 flats have electric cookers fitted currently, but there is a 15 mm copper gas supply present behind each cooker. Each of the gas supplys are capped off , pipe work is not identified or supported ( just hanging loose behind the cooker ) In the communal kitchen area these is a large electric cooker , again with a 15 mm gas pipe behind. This still had a bayonet elbow in place, this is a non permanent fitting . Elbow has been removed and capped off as req . Site have been verbally and visually informed, about contacting their gas supplier to replace the govenour. Also Jim Park from Karbon has been informed . Whilst on site the engineer from northen gas attended and replaced the ECV that is letting by as req . The engineer cannot replace the govenour , as this is the property/ responsibility of the site gas supplier . IVP - 0.271 m3 IVF - 0.0271 m3 IMV - 0.037 m3 Total - 0 3351 m3 SOS - the main office area - 30 m3 MAPD - 1.9 mb Result...... Pass , zero drop detected or recorded with appliances connected. Installation is AT RISK due to corroded pipe work externally , pipe work unventilated in ducts and non gas families ECVs fitted , corrosion to govenour on meter. Warning notices issued . LPC 25.3.21 0815 - 1630 Attended site to carry out annual gas saftey inspection on 7 x individual room sealed domestic combination boilers. Each boiler has been tested for safe operation, as per manufacturers instructions with 26.9 checks along side. There are 12 flats in total , every 2 x flats share a kitchen . The PRV pipe work that can be seen externally , is not returned to the wall so cannot be defused . Also the PRV pipe work from boiler in flat 7 & 8 is snapped off . I cannot follow the condensate line routes , to see how or where they run into . Flats 5 /6 and 11/12 have vertical flues fitted, I have gained access to the loft spaces above . I found the flues to in good condition, and operating ok . The flue from 11/12 has a bracket fitted . The flue from the boiler in flats 7/8 passes through a duct. The duct has an inspection hatch fitted, found flue to be ok . All flue terminals are in good condition , with the correct clearance. All flue sample point caps have been checked for damage on both sides , all found to be ok . Appliance details All boilers are Potterton Promax combi 28 , all readings acceptable in high and low fire modes . Working pressure tested in high fire mode again acceptable . Flats 1 /2 Promax combi 28 Sn , PXA162720130CC 28 kw not rated Location kitchen Flats 3/4 Promax combi 28 Sn , PXA17390020cc 28 kw not rated Location kitchen Flats 5/6 Promax combi 28 Sn , AWA114650054CC 28 kw not rated Location hall cupboard Toilet room Promax combi 38 Sn , PXA173930022CC 28 kw not rated Location toilet room LHS of building . Flats 7/8 Promax combi 28 Sn , PXA161440134CC 28 kw not rated Location kitchen Flats 9/10 Promax combi 28 Sn , PXA1739200009CC 28 kw not rated Location kitchen Flats 11/12 Promax combi 28 Sn , AWA120330333LC 28 kw not rated Location hall cupboard

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5498
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5498
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5498
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5498
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5498
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes