## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Osborne Villas
9 Osborne Avenue
Newcastle upon Tyne
NE2 1JU
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5500
DATE OF REPORT: 30/03/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5500
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Osborne Villas
9 Osborne Avenue
Newcastle upon Tyne
NE2 1JU
Carried Out On | 24/03/2021, 30/03/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 01.04.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5500
SECTION 3: Report
LPC 24.3.21 0905 - 1535 Attended site to carry out annual gas saftey inspection as req , on 2 x open flue potterton boilers and 1 x room sealed Vokera water heater . Each appliance has been tested for safe operation as per manufacturers instructions, with all 26.9 checks along side . Burners have not been removed , as specific Gaskets are req. Gained access to the plantroom where the 2 x potterton boilers are installed , both are B23 converted connected to a common flue system . Found the flue to leaking condensate badly in numerous places , with signs of previous repairs . Flue also had a mechanical trap fitted, these cannot be used on a flue system. Carried out extensive repairs to flue , removed and split leaking joints . Cleaned away corrosion and fitted new seals , rebuilt flue back to original state . Fitted new non mechanical traps as req , cut out leaking condensate pipework . Flue now performing ok , no leaking condensate etc . Combustion and cooling ventilation is supplied via a large wooden grill in the wall , at high level. An attempt to create high and level definition has been carried but this is not correct. The low level is not within the lower 15 % of the wall . The free air supplied is more than adequate, but not in the correct orientation. As these appliance are open flue B23 and not an atmospheric burner with a draught diverter , the ventilation is NCS . I have not been able to carry out a gas tightness test, due to the refuge shoot in use in front of the gas meter . The manager had not notified the Tennents that the shoot cannot be used , notification will be req . Found boiler no.1 LHS to be very noisy on high fire only , possibly a heat exchanger fault . Further investigation to be carried out and Gaskets will be req . Found GFA readings in both high and low fire modes to be acceptable . When working on boiler no.2 , I was unable to achieve satisfactory readings on high fire . The adjustment screw on the gas valve was fully wound out , and very loose . These gas valves have been know to leak when this screw goes like this. Gas supply has been capped off to boiler 2 and made safe , new gas valve and Gaskets req. There is a separate water heater that just supplies the laundry room . Again this has been tested as per manufacturers instructions, in both high and low fire modes . Found to operating safely, flue terminal has the correct clearance. Appliance details Water heater Vokera Aquanova Le 17 27 kw not rated Sn , 20143490PR180OO1087 High fire Burner pressure - 12 mb Low fire Burner pressure - 1.5 mb Boiler 1 LHS Potterton Sirius TWO FS 110 110 kw not rated GFA High fire 02 , 4.4 Co2 , 9.4 Co , 128 ppm Ratio , 0.0014 Low fire 02 , 4.6 Co2 , 9.2 Co , 4 ppm Ratio , 0.0000 Boiler 2 RHS Potterton Sirius TWO FS 110 110 kw not rated GAS SUPPLY CAPPED OFF, AS UNABLE TO ACHIEVE ACCEPTABLE GFA READINGS , NEW GAS VALVE REQ . LPC 30.3.21 0835 - 1050 Attended site and carried out annual commercial gas tightness test as per the guidance published in UP1A. The gas meter is located in a cupboard , off the storage shoot bin area . Both the bin store and gas cupboard door , have ventilation at high and low levels and communicate directly to outside. The gas transporters warning advice label is present and completed, on the wall behind the meter . Both the ECV ( wheelhead ) and the AECV are free moving , earth bonding present at the meter . Gas pipe work from the meter room into the plantroom , is not sleeved or fully sealed through the wall . Gas pipe work is partly identified along its route , to the boilers and water heater . The cupboard key is identified as THE GAS METER KEY , the cupboard externally is labelled as GAS CUPBOARD , the internal door also states GAS ECV LOCATED HERE. There is an emergency stop button at the plantroom door , when pressed the gas supply is isolated to the area via a solenoid valve. The controls are auto resetting and not manual, but this is existing installation . IVP - 0.0396 m3 IVF - 0.00396 m3 IMV - 0.067 m3 Total - 0.11056 m3 SOS - the plantroom- 30 m3 MAPD - 2.1 mb Letby - 2 minutes Stabilisation 6 minutes TTP - 2 minutes Result..... Pass , zero drop recorded or detected with appliances connected.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5500
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5500
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5500
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5500
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5500
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes