## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Shelley Court
Pelton Fell
Chester-le-Street
DH2 2QD
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5501
DATE OF REPORT: 01/04/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5501
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Shelley Court
Pelton Fell
Chester-le-Street
DH2 2QD
Carried Out On | 26/03/2021, 30/03/2021, 31/03/2021, 01/04/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 06.02.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5501
SECTION 3: Report
LPC 26.3.21 1110 - 1245 Attended to carry out annual gas safety inspection. Found plantroom to be liteally full of combustable materials , from fire alarm contractors . Removed items from plantroom and left tidy outside , karbon have been informed in turn who have informed the contractor. Items have been removed from site. Worked out gas pipework volume, but not tested. Note ...... Boilers , flue and gas pipe work etc have not been worked on or tested today. LPC 30.3.21 1300 - 1600 Attended site and carried out annual commercial gas tightness test, as per guidance published in UP1A. The primary gas meter is located in a cupboard to the LHS of the plantroom, at the main entrance to the building. The 2 x wooden doors have holes drilled at high level , to supply ventilation to the area . The gas transporters warning advice label is present and completed, in the wall behind the meter . Both the ECV and AECV are smooth operating , with labels of operation in their handles . Earth bonding is present at the gas meter . Pipe work is partly identified, as pipe work is steel over 1 " joints are welded . Pipework on the outlet side of the meter , has not been painted and has light surface corrosion and is not identified. There is a secondary gas meter located within the plantroom , this does not serve a purpose ( ideally should be removed as it's just increasing the pipework volume ) Pipe work from the primary meter through to the plantroom , is sleeved but not correctly sealed . There is a gas ECV fitted upon entry into the plantroom , for localised purposes. Purge and test points are present as are ECVS to each of the 3 x boilers installed . Pipe work is well supported along its route . There is an emergency stop button at the plantroom door , when pressed the gas supply is isolated to the area via a solenoid valve. The controls are auto resetting and not manual , this is an existing installation. I have attached a key ring to the plantroom key , as it was bot identified. The key ring reads "PLANTRROM AND GAS METER ) I have also attached a label to the gas meter cupboard door , again reads " THE GAS EMERGNCY CONTROL VALVE IS LOCATED IN HERE . IVP - 0.105 m3 IVP - 0.00105 m3 IMV - 0.067 m3 Total - 0.1825 m3 SOS - the plantroom - 50 m3 MAPD - 3.4 mb Letby - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result..... Pass , zero drop detected or recorded with appliances connected. There are 3 x Remeha quinta pro 115 boilers installed , all in B23 format in a common flue system. The flue has a condensate fitted , that has a non mechanical trap fitted . The flue itself visually appears to be in good condition. The flue then leaves the plantroom via the roof above vertically, sealed and fire stopped . Then the flue runs externally up the front of the building , before passing through the eaves of the main roof . The flue is touching the eaves in areas , no signs of scorching as the flue temps at this point will be very low . I do not know if the material used for the eaves is fire resistant or not . Finally the flue exits the main roof with a sealing weather collar . Attempted to gain access to loft space in main building , but literally full of contractors materials . Site is having a new fire alarm system installed and all fire protection materials installed . Unable to visually inspect flue in loft space , do not know if fire stopped or not . Combustion and cooling ventilation is supplied via 2 x large wooden Louvred doors. Both doors communicate directley to outside , the doors supply more than adequate ventilation to the area as measured and calculated . Boiler no.1 LHS is not running , there are numerous power PCB's on top of the appliance ( indicating an issue) I have carried out extensive testing in an attempt to locate, and repair fault . The parts req have been orderd with Spencer at border heating. Boilers not worked or tested today . LPC 31.3.21 0825 - 1030 Attended site and stripped down boiler no.2 middle . Replaced Gaskets and probes as req , service kit C . Tested for saftey as per manufacturers instructions, in both high and low fire modes . All 26.9 checks carried out . Boiler no.1 LHS - not running , boiler 3 RHS not worked in or tested today . Appliance details Boiler 1 LHS Remeha Quinta pro 115 115 kw not rated Sn , 1025700508180 NOT TESTED AS NOT RUNNING = NT Boiler 2 middle Remeha Quinta pro 115 115 kw not rated Sn , 1025700508190 GFA High fire 02 , 4.8 Co2 , 9.2 Co , 55 ppm Ratio , 0.0006 Low fire 02 , 6.3 Co2 , 8.3 Co , 23 ppm Ratio , 0.0003 Called off site to attend emergency calls elsewhere. LPC 1.4.21 0815 - 1005 Attended site and carried out service to boiler no.3 RHS , tested for safe operation as per manufacturers instructions. Gaskets have replaced along with probes , burner and heat ex inspected. All 26.9 checks carried out along tests in high and low fire modes . Appliance details Boiler 3 RHS Remeha Quinta pro 115 115 kw not rated Sn , 10270050820 GFA High fire 02 , 4.8 Co2 , 9.2 Co , 68 ppm Ratio 0.0007 Low fire 02 , 6.3 Co2 , 8.3 Co , 17 ppm Ratio , 0.0002

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5501
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5501
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5501
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5501
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5501
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes