## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Park House
Park Road
Sherburn
DH6 1EA
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5503
DATE OF REPORT: 26/04/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5503
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Park House
Park Road
Sherburn
DH6 1EA
Carried Out On | 06/04/2021, 07/04/2021, 26/04/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 28.04.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5503
SECTION 3: Report
LPC 6.4.21 10:00 - 1630 Attended site to carry out annual gas saftey inspection . The gas appliances on site consist of 1 x 56 kw boiler , 1 x 19 kw water heater and 2 x 7.9 kw hobs = 90.8 kw in total . The gas meter fitted is a U6 Domestic meter, capable of supplying approx 60 - 64 kw max . The water heater is located in the loft space and is open flue . There isn't any purpose installed combustion ventilation , just vents in the eaves , that the loft insulation has been pulled back . The flue is not correctly installed and is not sealed or secured , it does not have the correct clearances on the roof . The gas pipe work / meter is undersized , as working pressures are low . The heater is stood on standard chipboard flooring , that is already damaged and not a fire proof material. With the contributing factors the heater has been found to be IMMEDIATELY DANGEROUS. The quality of the installation of the heater is extremely poor . Gas supply has been capped off and made safe with a label attached and warning notice issued. The 2 x gas hobs in the kitchen do not have FSD's installed , and where found to be burning badly. Carried out an ambient co2 test with doors shut , but one window open. The reading readings recorded after only 4 minutes , where in the excess of 5000 ppm Again these are IMMEDIATELY DANGEROUS and gas supply to both appliances have been capped off and made safe . Also the gas meter is located approximately 6.5 feet in the air , and the ECV is extremely difficult to use and access. Site has been advised to contact northern gas networks , to inquire about having the gas meter lowered for better access . Both Jim Park and Chris Coffer have attended site and both agreed that the water heater and the hobs are IMMEDIATELY DANGEROUS. I have not worked on or tested the boiler today , nor Have I carried out a tightness test . LPC 26.4.21 1135 - 1205 LPC 26.4.21 1135 - 1205 LPC 26.4.21 1135 - 1210 Arrived on site and gained access to building ,proceeded to recently installed boilers . The install is not complete and gas pipework unsupported, from gas meter to the appliances . PRV from Cylinder not connected not ran to outside . Job reqs completing before gas cert or commission works can be carried out Asked by Dave Hunter to leave my Gas Annalyser on site , for him to use . Boilers and gas pipe work not worked on or tested today .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5503
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5503
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5503
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5503
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5503
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes