## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Rooms with Bungalow, 5 Carisbrooke Close
Washington
Tyne & Wear
NE37 2HZ
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5504
DATE OF REPORT: 16/04/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5504
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Rooms with Bungalow, 5 Carisbrooke Close
Washington
Tyne & Wear
NE37 2HZ
Carried Out On | 16/04/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 28.04.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5504
SECTION 3: Report
LPC 16.4.21 0955 - 1400 Attendeed site and carried out annual domestic gas saftey inspection as req . Carried out tightness test as per UP1B , and found to be gas tight . Gas meter is located externally in meter box ,22 copper sleeved through the wall , sealed with non setting putty. Gas transporters warning advice label is present and completed, gas ECV smooth operating with label of operation and earth bonding present . The gas meter is only a domestic U6 , whilst the 2 x appliances have a total heat input of nearly 80 kw . 22 mm copper is ran from the gas meter and to the boiler in the kitchen , but 28 mm at the water heater. By increasing the pipe work after the initial connection at the meter is pointless and will not achieve , extra volume , velocity or pressure . Carried out all req 26.9 checks and found the gas supply to largely undersized. When I tested the hot water and set up in high fire to carry out GFA , the working pressure was 11.5 mb at the gas valve . Also the water heater heater has a vertical flue that passes through the loft space, I have gained access to visually inspect . I found 1 x joint that cannot be inspected , flue is supported via metal tie wrap and not a flue bracket. There is also another unused vertical flue still in place in the loft space ( not connected to an appliance ) With the water heater isolated and just the boiler running , working pressure is ok . There is an unvented cylinder in the loft to do the main building. The water heater only seems to do the laundry room area. I have found the water heater to be AT RISK as at nearly 50 kw , a U6 meter and 22 mm pipe work cannot cope . Water heater has been isolated and made safe , warning label attached . Checked all taps other the laundry room , all unaffected and working ok . The gas appliances consist of 1 x room sealed Baxi boiler in the kitchen area and a room sealed water heater in the laundry ( no gas fires or cookers present ) Kitchen boiler Boiler has a standard flue kit and correct terminal . Condensate runs into drain externally . Tested boiler as per manufacturers instructions in both high and low fire, readings recorded. Replaced sample point as notch snapped Wooden boxing above boiler touching , outer plastic casing . Details Baxi 430 Heat Sn , 7668936 30 kw , not rated GFA High fire 02 , 4.5 Co2 , 9.3 Co ,56 ppm Ratio , 0.0006 Low fire 02 , 5.2 Co2 , 8.9 Co , 22 ppm Ratio , 0.0002 Water heater Worcester Wi 47 Greenspring WTD27 AME S505 48.4 kw ,not rated GFA High fire 02 ,6.7 Co2 , 8.1 Co , 24 ppm Ratio, 0.0003 Low fire 02 , 16.6 Co2 , 2.5 Co , 35 ppm Ratio , 0.0014

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5504
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5504
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5504
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5504
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5504
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes