## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Cockshaw Court
Hexham
Northumberland
NE46 3HU
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5506
DATE OF REPORT: 04/05/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5506
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Cockshaw Court
Hexham
Northumberland
NE46 3HU
Carried Out On | 04/05/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 29.05.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5506
SECTION 3: Report
LPC 4.5.21 10:00 - 1630 Attended site and carried out commercial gas tightness test, as per the guidance published in UP1A. The gas meter is located in a ventilated cupboard off the bin store area, at the front of the building . The bin store has a large wooden louverd door fitted , that communicates directly to outside. I have a attached a label to the gas meter cupboard , that states the gas meter is located in the LHS of this cupboard. The gas transporters warning advice label is present and completed. Both the ECV and AECV at the meter are free moving , the ECV falls to the closed position and has label of operation present. The AECV does not fall to the closed position and does not have a label of operation attached. Earth bonding present at gas meter and connected as req. The gas pipe work leaves the gas meter and runs vertically , then enters the ceiling place. The next visable of area of the gas pipework is within the plantroom area . It is not possible to visually inspect / follow the pipe work along its route, as it is ran underfloor / in the ceiling void area . The pipe work that is on show , is identified as GAS. I can only only assume its route , as no line diagram present on site . This was noted by Dave Aston on last year's visit , the installation is AT RISK and warning notice has been issued. The gas pipework enters the plantroom at high level , not sleeved and sealed with expanding foam . Pipework is identified with an AECV fitted for localised isolation purposes. Test and purge points are fitted to the pipe work as req. The pipe work tees off in 22 mm copper to supply the water heater , located next door in the laundry room ( not sleeved through the wall) The 2 x plantroom boilers have their manufacturers ECVS fitted , as does the water heater next door. There is an emergency stop button fitted at the plantroom door , when pressed the gas supply is isolated to the area via a solenoid valve. The controls are auto resetting and not manual , this is an existing installation. IVP - 0.033 m3 IVP - 0.0033 m3 IMV - 0.068 m3 Total - 0.1033 m3 S.O.S the laundry - 26 m3 MAPD - 1.8 mb Letby - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result... Pass , zero drop recorded or detected with appliances connected. Whilst on site carried out annual commercial gas saftey inspection on 2 x open flue potterton boilers in the plantroom, 1 x room Water heater in the laundry room . Each appliance has been tested for safe operation as per manufacturers instructions, with all 26.9 checks along side . Burners have not been removed or heat exchangers etc inspected , as Gaskets would be req . Boilers The 2 x potterton sirius TWO FS 70 boilers have been B23 converted , and are on a shared flue system. The flue has alot of staining present from previous leaks , that have been repaired , but not leaking now . The flue is suspended from the ceiling, then enters an old twin wall flue as a sleeve . I do not know if a liner has been used or not , the terminal can be clearly seen from the rear of the building . I have gained access to the loft space , where the vertical flue pass through . All that can can be seen the external side of the old twin walled flue . The condensate lines have been upgraded today , with a non mechanical trap being fitted . NOTE... I highly recommend getting a flue specialist to strip and inspect the seals in the flue . Also see if a better flue design is available. Ventilation for combustion and cooling purposes is supplied via a large wooden Louvred door. The door communicates directly to outside , and does not have fly screens fitted . The door does not have a true high and low definition, but supplies more that adequate ventilation for the appliances currently installed and calculated . Appliance details Boiler 1 LHS Potterton SIRIUS TWO FS 70 70 kw not rated GFA High fire 02 , 5.2 Co2 , 8.9 Co , 88 ppm Ratio , 0.0010 Low fire 02 , 5.9 C02 , 8.5 Co , 2 ppm Ratio , 0.0000 Boiler 2 RHS Potterton SITIUS TWO FS 70 70 kw not rated GFA High fire 02 , 5.1 Co2 , 9.0 Co , 99 ppm Ratio , 0.0011 Low fire 02 , 5.9 Co2 , 8.5 Co , 3 ppm Ratio , 0.0000 Water Heater Rinnai Infinity 16 REU 16FUA E 32 kw - not rated NOT TESTED AS NOT RUNNING - DAMAGE TO FLUE TURRET . Is located in the laundry room area , with a standard horizontal room sealed flue kit fitted. The appliance is displaying a E11 fault = no flame detected as is not running. I can assume that the appliance supplys the laundry and core areas , as the flats have their own DHW source . The appliance has not long been replaced and will be under warranty . Also the flue turret elbow is not sitting on the appliance connector correctly , a good seal is not being made . The elbow has a seem that locates and clips together , this is not fitting well either. As a safe measure the appliance has been isolated from the gas supply ( supply capped off ) Warning notice issued AT RISK , but was not running when found .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5506
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5506
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5506
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5506
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5506
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes