## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Renwick House
Abbey Meadows
Kirkhill
NE61 2BN
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5509
DATE OF REPORT: 10/05/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5509
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Renwick House
Abbey Meadows
Kirkhill
NE61 2BN
Carried Out On | 05/05/2021, 10/05/2021 10/05/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 12.06.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5509
SECTION 3: Report
LPC 5.5.21 Left home at 07:30 , arrived on site at 08:55 due to heavy traffic . 0855 - 1030 LPC 10.5.21 1125 - 1230 Attended site and carried out commercial gas tightness test, as per the guidance published in UP1A. The gas meter is located in a purpose brick built meter house , in the rear car park area . The housing has ventilation and a lockable door, the key is clearly identified. Both the ECV and AECV are free moving , complete with labels of operation . The gas meter is set on the ground , with no signs of corrosion . The gas transporters warning advice label is present and completed. Gas pipe work to the building has lights corrosion present , as it has not been painted for protection / identification. As the pipe work leaves the meter house , it is not sleeved through the wall or identified/ protected. I can only assume the route of the pipe work as the majority is ran below ground level ( below the carpark area) I have taken the straightest route ( no line diagram present on site) There is some type of tape wrapped protection on the pipe work, that is visable . Gas pipe work then enters the plantroom at low level , sleeved through the wall , earth bonding present upon entry . There is an old ECV fitted upon entry but the handle has long been removed . Found the spindle to be seized solid , it's clear that the handle has been removed to prevent confusion . There is an emergency stop button at the plantroom door , when pressed the gas supply is isolated to the area via a solenoid valve . The controls are auto resetting and not manual, this is an existing installation. Gas pipe work within the plantroom is fully identified and well supported along its route . Each appliance has it's on ECV fitted , test and purge points are also present . At the meter house the gas transporters PE pipe work is exposed ( northern gas networks informed ) Their works ref no - 5372 - 2159 Warning notice issued as AT RISK. Calculated total volume inorder to carry out test as per UP1A IVP - 0.12 m3 IVF - 0.012 m3 IVM - 0.067 m3 Total - 0.199 m3 S.O.S - the plantroom - 55 m3 MAPD - 3.8 mb Letby - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result...... Pass , zero drop recorded or detected with appliances. Warning Notice issued as gas transporters PE pipe work exposed.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5509
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5509
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5509
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5509
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5509
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes