## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Carlton Court
Scorer Street
North Sheilds
NE29 0LB
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 20-5554
DATE OF REPORT: 12/01/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5554
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Carlton Court
Scorer Street
North Sheilds
NE29 0LB
Carried Out On | 12/01/2021 24/12/2020, 13/01/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC including bungalows and communal boiler TD 18.01.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5554
SECTION 3: Report
LPC 23.12.20 1005-1010 Attended site but got called off to attend an emergency job elsewhere. LPC 24.12.20 0900 - 1155 Attended site and carried out commercial gas tightness test as per the guidance published in UP1A. Traced the gas pipe work along its entire route , then calculated the volume . The gas meter ( turbine ) is located in an external cupboard , to the LHS of the plantroom . The cupboard is well ventilate , as 2 x Louvred doors are fitted , the key is also identified . The gas pipe work after the meter has a small amount of surface corrosion present , reqs cleaning and repainting . The gas transporters warning advice notice is present and correct in the area . Gas pipe work is fully identified and well supported along its route to the boilers . The pipe work only sleeved on one side of the wall , as it enters the plantroom area. All ECVS and AECVS operate smoothly, pipe work has test and purge points installed . As pipe work is over 2 " the fittings are all welded , this is correct . IVP - 0.0756 m3 IVF - 0.00756 m3 IMV - 0.0037 m3 Total - 0.08586 m3 S.O.P - the plantroom - 40 m3 MAPD - 2.8 mb Let by - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result . Pass , zero drop recorded or detected with appliances connected. Whilst on site carried out annual gas safety inspection on the 3 x open flue (B23) hamworthy boilers . Appliances tested as per manufacturers instructions, with all 26.9 checks carried out alongside . Burners have not been removed ,for inspection as Gaskets would be req. Ventilation for combustion and cooling purposes is supplied, via 2 x large metal Louvred doors . Both doors communicate directley to outside, with large gauge gauze on the inside , that cannot easily become blocked. The doors do not have a true high and low definition, but supply adequate ventilation to the area to allow safe operation of the appliances . The gas supply enters the area at high level with an AECV upon entry for localised isolation purposes. Each appliance has it's own manufacturers ECV fitted. There is an emergency stop button fitted at the plantroom door , when pressed the gas supply is isolated to the area. The gas solenoid valve is interlocked to the gas supply , the controls are auto resetting and not manual, this is an existing installation. All 3 x modules are connected to one common flue , that runs at ceiling level . The flue has non mechanical traps fitted to it , to drain the condensate . The flue then enters a brick built chimney, that runs externally on the rear wall of the building . I do not know if the chimney is lined or not. There is a hard wired Co and Methane detector installed within the plantroom , I am unable to test this device . I have not worked on the appliances within the attached bungalows , only the communal plant. Appliance details Top module no.1 Hamworthy Fleet F125V Sn , F 12VF161GB 02548H GFA High fire 02 , 5.1 Co2 , 9.0 Co 38 ppm Ratio , 0.0004 Low fire 02 , 5.0 Co2 , 9.0 Co , 13 ppm Ratio , 0.0001 Middle module no.2 Hamworthy Fleet F125V sn , F12VF161GB 02527H GFA High fire 02 , 5.0 Co 2 , 9.0 Co ,147 ppm Ratio , 0.0016 Low fire 02 , 4.8 Co2 , 9.1 Co , 36 ppm Ratio , 0.0004 Bottom module no.3 Hamworthy Fleet F125V Sn , F12VF161GB 02546H GFA High fire 02 , 5.0 Co2 , 9.0 Co 85 ppm Ratio , 0.0009 Low fire 02 , 5.0 Co2 , 9.0 Co , 22 ppm Ratio , 0.0002 LPC 12.1.21 unable to locate Gaskets LPC 12.1.21 1200 -1425 Arrived on site and gained access to plantroom area , began stripping top module to replace gaskets . Dave Hunter arrived with service kits . When I opened the Kits I found that the Burner Gasket was not present in the sets . Also my Testo Gas Annalyser would not power up , spoke to technical, but unit reqs returning to Testo for repair .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5554
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5554
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5554
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5554
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5554
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes