## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Eldon Court
Clavering Street
Willington Quary
NE28 6SW
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 20-5556
DATE OF REPORT: 29/01/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5556
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Eldon Court
Clavering Street
Willington Quary
NE28 6SW
Carried Out On | 29/01/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 11.02.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5556
SECTION 3: Report
LPC 29.1.21 0830 - 1530 Attended site and carried out commercial gas tightness test as per the guidance published in UP1A. The gas meter is a boundary meter (U40) , located in a plastic ventilated meter housing in the front garden area . Both the ECV and AECV are freely moving , complete with labels of operation . Gas transporters warning advice notice also present at the meter . Gas pipe work is wrapped in denzo tape , as the majority of the pipe work is ran below ground level. Traced pipe work along its straightest route , then calculated the volume as req . Gas pipe work enters the plantroom at low level and sleeved through the wall. Wheel head type fitted upon entry, for localise isolation purposes . Pipe work is fully identified and supported along its route, test and purge points present throughout . There is an emergency stop button fitted at the plantroom door , connected to a solenoid valve. When the button is pressed the gas supply is isolated to the area. The interlock controls are auto resetting , and not manual as per UP2 , this is an existing installation. IVP - 0.162 m3 IVF - 0.0162 m3 IVM - 0.067 m3 ( G25 / U40) Total - 0.2452 m3 S.O.S - The plantroom > 60m3 MAPD - 4.2 mb Let by - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result.... Pass , zero drop recorded or detected with appliances connected. Carried out whilst on site annual commercia gas saftey inspection . Appliances tested as per manufacturers instructions, with all 26.9 checks out along side , to ensure safe operation. The appliances on site consist of 2 x Lochinvar water heaters , and 3 x Hamworthy modular boilers. Every appliance is open flue ( B23) Burners have been removed from the 3 boiler modules , to allow cleaning and inspection etc . Gaskets with probes have been replaced as req . Burners have not been removed from 2 x water heaters , as readings are well with manufacturers specifications. The gas valve on boiler module no.2 , the low fire adjustment screw is Bradley chewed. This is only plastic and is in the form of a torx , fortunately the low fire did not req a lot of adjustment. I would highly reccomend fitting a new gas valve in the near future . Combustion ventilation is supplied via 2 x large metal grill in the wall , at high and low levels . Both vents communicate directly to outside , with vermin mesh fitted , that is over 5 mm in diameter as per BS 6644 The Vents installed supply more than adequate ventilation , for combustion and cooling purposes as measured and calculated . The 2 x water heaters are connected to their own common flue system . The flue in good physical condition and well supported , no signs of corrosion or leaks . The condensate lines have non mechanical traps fitted. The 3 x modular boilers have their manufacturer specific plastic flue manifold fitted , at the rear that links all modules. The manifold then runs into a stainless flue , that again is well supported along its route . This flue also has non mechanical traps fitted to the condensate lines , no signs of corrosion or leaks present. Both flues then separately enter a brick built chimney , I do not know if the chimney is lined or not etc. Plaster board has been used to seal the flues into the chimney opening, I do not know if this is fire rated or not etc. Both flue terminals can be clearly see from the front of the building . Appliance details Water heater 1 LHS Lochinvar SHW 46 325 NG CE Sn , 1637103420387 GFA High fire 02, 5.0 Co2 , 9.0 Co , 31 ppm Ratio , 0.0003 Low fire 02 , 5.2 Co2 , 8.9 Co , 7 ppm Ratio , 0.0000 Water heater 2 RHS Lochinvar SHW46 325 NG CE Sn , 1637203420388 GFA High fire 02 , 5.3 Co2 , 8.9 Co , 33 ppm Ratio , 0.0003 Low fire 02 , 4.8 Co2 , 9.2 Co , 4 ppm Ratio , 0.0000 Module no 1 top Hamworthy Fleet F50V Sn , F5VG161GB 02595H GFA High fire 02 , 5.0 Co2 , 9.0 Co , 36 ppm Ratio , 0.0003 Low fire 02 , 5.0 Co2 , 8.0 Co , 17 ppm Ratio , 0.0001 Module no 2 middle Hamworthy Fleet F50V Sn , F5VG161 GB 02594H GFA High fire 02 ,5.0 Co2 , 9.0 Co , 25 ppm Ratio , 0.0002 Low fire 02 , 5.2 Co2 , 8.9 Co , 11 ppm Ratio , 0.0001 Module no 3 bottom Hamworthy Fleet F50V Sn , F5VG161 GB 02593H GFA High fire 02 , 5.1 Co2 , 9.0 Co , 42 ppm Ratio , 0.0004 Low fire 02 , 4.9 Co2 , 9.1 Co , 22 ppm Ratio , 0.0002

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5556
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5556
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5556
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5556
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5556
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes