## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Preston Court
Roseberry Avenue
North Sheilds
NE29 9PG
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 20-5557
DATE OF REPORT: 02/02/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5557
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Preston Court
Roseberry Avenue
North Sheilds
NE29 9PG
Carried Out On | 02/02/2021, 03/02/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 11.02.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5557
SECTION 3: Report
LPC 2.2.21 0830 - 1250 Attended site and carried annual commercial gas tightness test ,as per the guidance published in UP1A . The gas meter is located in a brick built out building, with a fully louverd metal door that provides ventilation. The meter location is at the side of the building , just in front of the plantroom, it has a white metal door fitted. Both the ECV and AECV are smooth operating , complete with labels of operation . A line diagram is mounted at the gas meter and in the plantroom. The gas transporters warning advice notice , is fixed to the wall behind the meter . The pipe work on the outlet side of the meter , is lightly corroded as it has not been painted . This will req cleaning with a steel brush and painting . Pipe work from the meter to the plantroom , run below ground level . Gas pipe work enters the plantroom at ground level , pipe work is wrapped in denzo tape for protection . Wheel head type valve fitted upon entry , for localised isolation purposes. Pipe work is identified within the plantroom , well supported along its route . Purge and test points are present , each boiler module has it's own ECV fitted . There is an emergency stop button fitted at the plantroom door , when pressed the gas supply is isolated to the area , via the solenoid valve . The controls are auto resetting as not manual , this is an existing installation . Used line drawing supplied , traced pipe work along its entire route, calculate volume as req . IVP - 0.0756 m3 IVP - 0.00756 m3 IMV - 0.067 m3 Total - 0.15016 m3 S.o.S - the plantroom > 60 m3 MAPD - 4.1 mb Let by - 1 minutes Stabilisation - 6 minutes TTP , 2 minutes Result... Pass , zero drop detected or recorded with appliances connected. Carried out annual gas saftey inspection and services 3 x hamworthy boiler modules. Appliances have been tested for safe operation as per manufacturers instructions , with all 26.9 checks along side as req . Each burner has been removed for inspection etc , Gaskets and probes replaced as req . Combustion ventilation is supplied via 2 x large metal grills in the wall at high and low levels. Both vents communicate directly to outside , vermin mesh is fitted on the inside , this is over 5 mm in diameter as per BS6644. The Vents supply more than adequate ventilation, to allow safe operation of the appliances fitted , as measured and calculated . The modules have their manufacturers specific plastic flue manifold fitted . The manifold is then connected to a stainless steel flue system , that is suspended from the ceiling via rods . The flue runs horizontally then enters a brick built chimney , that runs vertically through the building. The flue liner can be see from the plantroom , as the chimney has not been sealed The flue has non mechanical traps fitted , as do each module and the flue manifold . The plastic waste pipe fitted after the traps , is leaking Bradley on to the floor. This is after the traps so just condensate , someone has put a plastic bag underneath the pipe work . The pipe work reqs cutting out and replacing . Appliance details Module 1 top Hamworthy Fleet F125V Sn , F12VE161GB 02505H GFA High fire 02 - 4.9 Co2 , 9.1 Co , 38 ppm Ratio , 0.0004 Low fire 02 , 5.4 Co2 , 8.8 Co , 31 ppm Ratio , 0.0003 Module 2 middle Hamworthy Fleet F125V Sn , F12VE161GB 02504 H GFA High fire 02 , 5.1 Co2 , 9.0 Co , 81 ppm Ratio , 0.0008 Low fire 02 , 4.9 Co2 , 9.1 Co , 36 ppm Ratio , 0.0003 Module 3 bottom Hamworthy Fleet F125V Sn , F12VE161GB 02503H GFA High fire 02 , 5.0 Co2 , 9.0 Co , 64 ppm Ratio , 0.0007 Low fire 02 , 5.3 Co2 , 8.8 Co , 1 ppm Ratio , 0.0000

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5557
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5557
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5557
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5557
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5557
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes