## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Rosebank Hall
Willington Terrace
Wallsend
NE28 7BT
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 20-5680
DATE OF REPORT: 05/02/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5680
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Rosebank Hall
Willington Terrace
Wallsend
NE28 7BT
Carried Out On | 04/02/2021 05/02/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 02.03.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5680
SECTION 3: Report
LPC 4.2.21 1400 - 1630 Attended site and carried out annual commercial gas tightness test as per the guidance published in UP1A. The gas meter is located in a brick outer building , beneath pavement level. You walk down 7 steps ( access the gas meter and plantroom) that are situated at the front of the building . There is a padlocked gate at the top of the steps. The area that the meter is located in is prone to dampness , as it has 2 " of water present under foot . Access to the ECV is very poor , due to its location . The steel pipe work is showing signs of corrosion , due to the damp environment. The gas transporters warning advice notice, is unreadable due to the water ingress . There are 2 x air bricks present to supply ventilation to area, these are blocked solid with moss and dirt . The door to the area has a label attached , that reads " GAS SHUT OFF VALVE " The door is not locked as the gate at the top of the stairs is kept locked. There is an AECV fitted after the meter that has a label of operation, and is operating smoothly . The pipe work is identified both in the gas meter area , and within the plantroom . Pipe work is sleeved through the wall and wrapped in denzo tape for protection. There needs to be works carried out to better water proof the gas meter location, possibly bunding the area . The pipe work then enters the plantroom at low level , with an ECV for localised isolation purposes. There are 2 x engency stop buttons installed in the plantroom, when either one is pressed the gas supply is isolated to the area. There is a large gas solenoid valve fitted, that is actuated via the stop buttons. The interlock controls are auto resetting and not manual, but this is an existing installation. Earth bonding is present to gas pipe work , within plantroom area . Traced gas pipe work along entire route, then calculated total volume to carry out test . IVP , 0.054 m3 IVF , 0.0054 m3 IMV , 0.0027 m3 Total , 0.0621 m3 S.O.S - the plantroom - > 60 m3 MAPD - 4.2 mb Let by - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result..... Pass , zero drop detected or recorded with appliances connected . Warning notice issued as AT RISK due to corrosion will carry on gets worse , until water proof works are carried out . There are 3 x room sealed Remeha boilers installed, mounted on a jig /Frame . The flues all run vertically and pass through the flat roof above. The flues do not have brackets fitted , but are solid to the touch . The terminals can be seen from the front of the building , with the use of ladders. Each of the flue has it's own condensate line, each line has a non mechanical trap fitted . There are 2 x grills in the wall at high and low level , both grills communicate directly to outside. The ventilation installed in adequate for cooling purposes . NOTE ......... BOILERS HAVE NOT BEEN WORKED ON OR TESTED TODAY. LPC 5.2.21 1330 - 1630 Carried annual gas saftey inspection on the 3 x room sealed boilers installed . Removed each burner inspected and cleaned heat exchangers, replaced gaskets and probes as per manufacturers instructions. Tested for safe operation with all 26.9 checked carried out found boiler no.2 middle to be IMMEDIATELY DANGEROUS , as internal flue and seals have failed. The flue has allowed products of combustion to escape , that has damaged all internal plastics ( turned yellow and brittle ) The internal light has crumbled the electric internal cover , has cracked and now offers no protection . 28 mm gas supply cut and capped to appliance, made safe . Warning notice issued and label attached . Appliance details Boiler 1 LHS Remeha Quinta pro 115 115 kw - not rated Sn , 1113702350730 GFA High fire 02 , 59 Co2 , 9.0 Co , 28 ppm Ratio , 0.0003 Low fire 02 , 5.7 Co2 , 8.6 Co , 1 ppm Ratio 0.0000 Boiler 2 middle Remeha Quinta pro 117 115 kw - not rated Sn , 1113702350700 NOT TESTED AS IMMEDIATELY DANGEROUS Boiler 3 RHS Remeha Quinta pro 115 115 kw , not rated Sn , 1113702350710 GFA High fire 02 , 4.9 Co2 , 9.1 Co , 53 ppm Ratio , 0.0005 Low fire 02 , 5.9 Co2 8.5 Co , 73 ppm Ratio , 0.0008 NOTE ..... Boiler no2 req new inner flue and an an attempt to tidy up internal plastics. New inner flue has been ordered with Steve at silver link parts Centre.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5680
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5680
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5680
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5680
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5680
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes