## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Rudyerd Court
Lower Rudyerd Street
North Sheilds
NE29 6PD
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 20-5681
DATE OF REPORT: 26/02/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5681
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Rudyerd Court
Lower Rudyerd Street
North Sheilds
NE29 6PD
Carried Out On | 24/02/2021 25/02/2021 25/02/2021 26/02/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 06.03.21

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5681
SECTION 3: Report
LPC 25.2.21 0830 - 1440 Attended site to carry out annual commercial gas tightness test as per the guidance published in UP1A. Found that gas transporters ECV is letting by , this has been reported to 0800 111 999. An engineer attended and confirmed that valve is letting roughly 1.75 mb in 2 minutes . The engineer managed to reduce the letby , but valve req replacement. This is being monitored by northern gas network , gas meter has 2 x AECVS fitted in outlet of meter . Gas supply can still be isolated to building via AECVS. Warning label has been attache to main ECV as not in use. Job no issued from gas emergency phone call - 5365 2425. Warning notice has been issued as AT RISK. Carried out emergency temporary repairs to common flue and leaking badley. Found to be AT RISK as numerous repairs have been carried out , flue reqs replacing co detector present . Warning notice issued LPC 26.2.21 0820 - 1350 Attended site and carried out annual commercial gas saftey inspection , on the 3 x Remeha boilers installed . Each appliance has been tested for safe operation , as per manufacturers instructions with all 26.9 checks also. Boiler no.1 is has only been installed for approx 6 months , the burner has not been removed . Both boilers 2 & 3 have the burners removed for inspection , heat exchangers cleaned ex. New Gaskets and probes have been fitted to boilers 2 & 3 as req . Ventilation for combustion and cooling purposes is supplied via , 2 x large grills in the wall at high angle low level. Also the plantroom doors have louverd installed at high and low levels . All ventilation communicates directly to outside, and is more than adequate to allow safe operation of the appliances installed. The 3 x boilers installed are open flue in B23 configeration , all connected to a common flue . The flue header is suspended from the ceiling with rods , and is secure to the touch . There is evidence of previous repairs along the flue , but no signs of corrosion or condensate leaks present at this time . The flue then runs into a brick built chimney with a large sealing plate fitted . I do not know if the chimney is lined or not , the terminal can be clearly seen from the rear of the building . The flue has one non mechanical trap fitted , there is provision for another condensate line . This is capped off with a galvanised cap as not in use . I would recommend getting a flue specialist to attended site , to possible look at replacing the flue in the near future . There is a emergency stop button fitted on the wall next the plantroom door, when pressed the gas supply is isolated to the area , via a solenoid valve. The controls are auto resetting and not manual , this is an existing installation. The gas pipe work is identified and well supported, along its route . A tightness has not been carried out, due to the ongoing issue regarding the gas transporters ECV letting by . Appliance details Boiler 1 LHS Remeha Quinta Ace 115 115 kw not rated Sn , 2014623821540 GFA High fire 02 , 4.8 Co2 , 9.1 Co , 53 ppm Ratio , 0.0006 Low fire 02 , 6.3 Co2 , 8.3 Co , 11 ppm Ratio , 0.0001 Boiler 2 middle Remeha Quinta pro 115 115 kw not rated Sn , 1113703351040 GFA High fire 02 , 4.9 Co2 , 9.1 Co , 58 ppm Ratio , 0.0006 Low fire 02 , 4.9 Co2 , 9.1 Co , 9 ppm Ratio , 0.0001 Boiler 3 rhs Remeha Quinta pro 115 115 kw not rated Sn , 1729217262000 GFA High fire 02 , 4.9 Co2 , 9.1 Co , 48 ppm Ratio , 0.0005 Low fire 02 , 4.8 Co2 , 9.1 Co , 8 ppm Ratio , 0.0001

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5681
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5681
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5681
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5681
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5681
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes