## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Phoenix Rise
Ambassadors Way
North Shields
NE29 8SQ
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 20-5682
DATE OF REPORT: 18/03/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5682
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Phoenix Rise
Ambassadors Way
North Shields
NE29 8SQ
Carried Out On | 18/03/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 25.03.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5682
SECTION 3: Report
LPC - CS 16.3.21 1425 - Attended site and made a start on annual gas saftey inspection as req . Measured and calculated combustion and cooling ventilation , found ventilation installed to be adequate . Found that flue manifold on boilers had been drilled to allow GFA to be carried out . Holes just taped over , drilled all 3 x holes to correct size of 12 mm and fitted Regin sample point plugs . Repaired leaking condensate lines from water heaters . Calculated gas pipe work volume inc meter , inorder to carry out test . 0910 - 1620 Attended site and carried out annual gas commercial tightness test , as per the guidance published in UP1A. The gas meter is located at the rear of the building , next to the plantroom in a public walkway. The meter is housing is a purpose built plastic structure , that is kept locked . The gas transporters warning advice label is present and completed . Both ECV and AECV are smooth operating with label of operation attached . Pipe is sleeved through into the plantroom, fully identified and well supported along its route. Purge and test points installed , each appliance has it's own ECV fitted . Upon entry the plantroom ECV is fitted to allow local isolation. There is an emergency stop button fitted at the plantroom door, when pressed the gas supply is isolated to the area. Via a solenoid valve that is interlocked, controls are auto resetting and not manual, this is an existing installation. IVP - 0.0756 m3 IVF - 0.00756 m3 IMV - 0.182 m3 Total - 0.26516 m3 SOS - Plantroom > 60 m3 MAPD - 3.9 mb Letby - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result... Pass , zero drop recorded or detected with appliances connected. Whilst on site carried annual gas saftey inspection , on 2 x open flue water heaters and 3 x open flue boiler modules . Each appliance has been tested for safe operation as per manufacturers instructions, with 26.9 checks along side . Burners have not been removed from water heaters , as readings are acceptable ( as per manufacturers instructions) Again burners not removed from boilers modules , as modules have not long been replaced been replaced under warranty . Combustion and cooling ventilation, is supplied 2 x large grills in the wall at high and low levels. Both Vents communicate directley outside , vermin mesh present over 10 mm in diameter. Measured and calculated total free air ,more than adequate to allow safe operation of appliances currently installed . The 3 x boiler modules are connected to a manufacturer specific manifold system, with non mechanical traps fitted . A stainless flue is then connected , that enters a purpose built external chimney . Both water heaters are connected to a common flue system, that is suspended from the ceiling. Flue has non mechanical traps fitted, that have had numerous repairs carried out. Ideally the entire condensate line req replacing . The flue then enters the purpose built chimney area , but the bottom of the flue is actually touching the wooden structure of the building . There is no signs of scorching or burning at time of testing , this reqs the wood beneath cutting away. I do not know if the wooden structure is fire rated or not , flues should have a minimum of 25 mm clearance from any combustable surface/ material. Appliance details Module 1 top Hamworthy Fleet F85V Sn , F8VK161GB 02196H 85 kw not rated GFA High fire 02 , 5.0 Co2 , 9.0 Co , 44 ppm Ratio , 0.0005 Low fire 02 , 5.1 Co2 , 9.0 Co , 6 ppm Ratio , 0.0001 Module 2 middle Hamworthy Fleet F85V Sn , F8VK161GB 21995H 85 kw not rated GFA High fire 02 , 4.8 Co2 , 9.1 Co , 139 ppm Ratio 0.0015 Low fire 02 , 4.9 Co2 , 9.1 Co , 8 ppm Ratio , 0.0001 Module 3 bottom Hamworthy Fleet F85V Sn , F8VK161GB 02194H 85 kw not rated GFA High fire 02 , 5.0 Co2 , 9.0 Co , 61 ppm Ratio , 0.0007 Low fire 02 , 5.0 Co2 , 9.0 Co , 8 ppm Ratio ,0.0001 Water heater 1 LHS Lochinvar SHW 61 325 NG CE Sn , B15C20332129 55.5 kw not rated GFA High high 02 , 5.5 Co2 , 8.8 Co , 29 ppm Ratio , 0.0003 Low fire 02 , 6.3 Co2 , 8.3 Co , 15 ppm Ratio , 0.0002 Water heater 2 RHS Lochinvar SHW 61 325 NG CE Sn , C15C20332127 55.4 kw not rated GFA High fire 02 , 5.6 Co2 , 8.7 Co , 32 ppm Ratio , 0.0004 Low fire 02 , 6.2 Co2 , 8.3 Co , 9 ppm Ratio , 0.0001

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5682
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5682
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5682
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5682
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5682
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes