## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Percy Lodge
St Johns Terrace
Percy Main
NE29 6JT
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 20-5694
DATE OF REPORT: 18/02/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5694
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Percy Lodge
St Johns Terrace
Percy Main
NE29 6JT
Carried Out On | 10/02/2021, 18/02/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 10.03.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5694
SECTION 3: Report
LPC 18.2.21 0820 - 1445 Attended site and carried out commercial gas tightness test as per the guidance published in UP1A. The gas meter is located in a brick built meter house , confront of the plantroom. The housing is ventilated with a locked door , the key is identified as" GAS METER KEY " The ECV and AECV are smooth operating with label of operation present. Gas transporters warning advice notice is mounted behind the meter . The pipe work from the meter is showing significant signs of corrosion, as it untreated steel. The pipe work is not leaking currently, but will req cleaning with a wire brush then painting . This is AT RISK and a warning notice has been issued . The pipe work from the meter to the plantroom , is ran below ground level. There is a line diagram present in the meter cupboard, this has been to calculate the volume . Pipe work within the plantroom is identified and well supported. Traced the gas pipe work along its entire route , then calculated the total volume as req . IVP - 0.6528 m3 IVF - 0.06528 m3 IVM - 0.067 m3 Total - 0.78508 m3 S.O.S the plantroom - 50 m3 MAPD - 3.5 mb Let by - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result.. Pass , zero drop recorded or detected with appliances connected. Whilst on site carried out annual gas saftey inspection , on the 3 x open flue boiler modules . Appliances have been tested for safe operation as per manufacturers instructions, with all 26.9 checked carried out. Would recommend replace burners on the modules , as starting fray . Managed to obtain acceptable GFA reading , but burners will only get worse . Found bottom module to have a bad leak from the flow switch , I have repaired this but damage has taken place . Combustion ventilation is supplied via 2 x large metal louverd door , and 2 x grills in the wall at high and low level. Just with the doors alone the ventilation in place , is more than adequate. The door have a large mesh on the inside , this is 10 mm in diameter. The grills in the wall have a smaller mesh fitted , but these are ideal for cooling purposes. There is an emergency stop button fitted at the plantroom door , when pressed the gas supply is isolated to the area. The solenoid is situated at low level and is interlocked to the gas supply . The controls are auto resetting and not manual, but this is an existing installation. All 3 x modules are connected via there own manufacturers specific, flue manifold system. The manifold is then connected to stainless steel flue system , suspended from the ceiling. The flue then leaves the plantroom , and enters avoid in the bin store . Flue then runs vertically through the same void on the next floor , there is not an inspection hatch fitted in the bin store on this level. I then gained access to the loft space and visually inspected the flue . The flue has non mechanical traps fitted, as does each individual module . As a safe measure a Co detector has been installed in each bin store , where the flue passes through. Appliance details Module 1 top Hamworthy Fleet F125V 125 kw not rated GFA High fire 02 , 5.1 Co2 , 9.0 Co , 45 ppm Ratio , 0.0005 Low fire 02 , 5.0 Co2 , 9.0 Co , 37 ppm Ratio , 0.0004 Module 2 middle Hamworthy Fleet F125V 125 kw not rated GFA High fire 02 , 5.0 Co2 , 9.0 Co , 74 ppm Ratio , 0.0008 Low fire 02 , 5.1 Co2 , 9.0 Co , 16 ppm Ratio , 0.0002 Module 3 bottom Hamworthy Fleet F125V 125 kw not rated GFA High fire 02 , 5.1 Co2 , 9.0 Co , 67 ppm Ratio, 0.0007 Low fire 02 , 5.1 Co2 , 9.0 Co , 15 ppm Ratio , 0.0002 Warning notice issued as flue only has 1 x inspection hatch installed , flue is under positive pressure in a void. AT RISK.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5694
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5694
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5694
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5694
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5694
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes