## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Eccles Grange
Church Road
Backworth
NE27 0FW
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 20-5705
DATE OF REPORT: 16/03/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5705
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Eccles Grange
Church Road
Backworth
NE27 0FW
Carried Out On | 15/03/2021, 16/03/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 25.03.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5705
SECTION 3: Report
LPC - CS 15.3.21 1400 - 1625 Attended site and carried out annual commercial gas tightness test as per the guidance published in UP1A. The gas meter is located in an out building to the LHS of the plantroom, at the front entrance off the car park area . The area is ventilated via 2 x grills in the door , both communicate directly to outside. The gas transporters warning advice is present and completed. Both the ECV and AECV are smooth o perating and fall to the closed position, with labels of operation present. Gas pipe work is bonded at the gas meter . Measured pipe work along its entire route , then calculated the total volume as req . Pipe work leaves the gas meter and enters the plantroom at low level , sleeved and sealed through the wall . Gas ECV fitted upon entry to the plantroom, for localised isolation purposes. Pipework is fully identified and supported along its route , with test and purge points present . There is an emergency stop button at the plantroom door, when pressed the gas supply is isolated to the area via a solenoid valve. The controls are auto resetting and not manual , this an existing installation. Pipe work is mainly 3 " steel and fittings are welded as req. IVP - 0.0702 m3 IVF - 0.0070W m3 IMV - 0.100 m3 Total - 0.08722 m3 S.O.S - the plantroom - > 60 m3 MAPD - 4.2 mb Letby - 2 minutes Stabilisation - 6 minutes Stabilisation - 2 minutes Result ..... Pass , zero drop recorded or detected with appliances connected. NOTE ....... BOILERS NOT WORKED OR TESTED TODAY LPC - CS 16.3.21 0835 - 1410 Attended site and carried out commercial annual gas saftey inspection , on 2 x open flue Hamworthy boiler modules . Burners have been removed for inspection and heat exchangers cleaned . Replaced Gaskets and fitted new ignition , ionisation probes . Tested both modules in high and low fire modes , as per manufacturers instructions, along with all 26.9 checks . Found both burners to be showing signs of wear , as gauze is deterating in areas. Found GFA to acceptable at time of testing , but would highly reccomend fitted new burners soon . Combustion and cooling ventilation is supplied via 2 grills in the wall at high and low levels . Plantroom doors also grills installed at high and low levels , all vents communicate directly to outside. Calculated total free air space of Vents fitted , found to be more than adequate for the appliances installed. Both modules are connected to a common flue system, that runs vertically through the building . I have attempted to trace the flue along its route for inspection . I have gained access to the loft spaces and again cannot visibility inspect the flue . The flue within the plantroom has light corrosion present , both modules have non mechanical traps fitted . The flue terminal can clearly be seen from the front of the building , but unable to locate internally . Appliance details Module 1 top Hamworthy Fleet F250V 250 kw not rated Sn , F25VE141GB 01000F GFA High fire 02 , 4.9 Co2 , 9.1 Co , 38 ppm Ratio , 0.0004 Low fire 02 , 3.4 Co2 , 9.9 Co , 5 ppm Ratio , 0.0001 Module 2 bottom Hamworthy Fleet F250V 250 kw not rated Sn , F25VE141GB 00999F GFA High fire 02 , 4.7 Co2 , 9.2 Co , 131 ppm Ratio , 0.0015 Low fire 02 , 3.5 Co2 , 9.9 Co , 5 ppm Ratio , 0.0001

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5705
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5705
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5705
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5705
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5705
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes