## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Rothley Grange
Solway Avenue
Cullercoats
NE30 3AU
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 20-5706
DATE OF REPORT: 12/04/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5706
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Rothley Grange
Solway Avenue
Cullercoats
NE30 3AU
Carried Out On | 12/04/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 28.04.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5706
SECTION 3: Report
LPC 12.4.21 0840 - 1300 Attended site and carried out commercial gas tightness test as per the guidance published in UP1A. The gas meter is a boundary meter , located in the front garden of the building . The meter is in a purpose built plastic housing , with ventilation and a lockable door. There is a plastic notice attached to the meter housing , that reads - GAS SHUT OFF VALVE . The gas transporters warning advice label is present and correct . Both the ECV and AECV are smooth operating, complete with labels of operation . There is a small amount of surface corrosion present to the pipework at the meter . I have traced the gas pipe work along its route , best as possible as the majority is ran below ground level. Calculated the total volume, inorder to carry out test. The gas pipework enters the plantroom at low level , sleeved through the wall ( not sealed as req ) Gas isolation fitted upon entry to allow localised isolation, earth bonding present. Pipework is fully identified and well supported along its route the appliances . Purge and test points present throughout the installation. There is a emergency stop button fitted at the plantroom door, when pressed the gas supply is isolated to the area via a solenoid valve. Controls are auto resetting and not manual, this is an existing installation. IVP - 0.432 m3 IVF - 0.0432 m3 IMV - 0.067 m3 Total - 0.5422 m3 S.O.S - the plantroom > 60 m3 MAPD - 3.6 mb Letby - 3 minutes Stabilisation - 6 minutes TTP - 4 minutes Result..... Pass , zero drop recorded or detected with appliances connected. Whilst on site carried annual commercial gas saftey inspection as req , on 2 x open flue water heaters and 3 x open boiler modules . Each appliance has been tested for safe operation as per manufacturers instructions, with all 26.9 checks carried out along side . Burners have not been removed as all GFA readings , found be acceptable and well within manufacturers specifications. Gaskets and probes have not been replaced , as not req . Combustion and cooling ventilation is supplied via 2 x large grills in the wall , at both high and low levels . Each vent communicates directly to outside , with vermin mesh fitted that is 10 mm wide. The ventilation installed in more than adequate to allow safe operation of the appliances , as measured and calculated. The 2 x water heaters are both connected to their own common flue system , that is suspended from the ceiling. The flue enters a purpose brick built external chimney , I do not know if a liner is fitted or not. The flue terminal can be clearly seen , the flue has condensate lines with non mecanical traps fitted . The flue is is good physical condition , with no signs of corrosion, repairs or leaks etc. Called to attend an emergency on another site

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5706
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5706
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5706
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5706
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5706
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes