## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Cheviot View
West Street
West Allotment
NE27 0RA
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 20-5707
DATE OF REPORT: 06/04/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5707
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Cheviot View
West Street
West Allotment
NE27 0RA
Carried Out On | 13/04/2021 19/04/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 30.04.2021 Finish mechanical works from service.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5707
SECTION 3: Report
LPC 13.4.21 0840 - 1505 Attended site and carried out annual gas saftey inspection , on 3 x open flue boiler modules . Each of the modules have had its burner removed, cleaned and inspected . Heat exchangers cleaned and again inspected , gaskets and probes also replaced . Each module has been tested for safe operation as per manufacturers instructions, with all 26.9 checks along side. Found all the gauze on the burners to be in poor condition, and req replacing asap , but not affecting safe operation at this time. The condition of the burners will only get worse . Ventilation for combustion and cooling purposes, is supplied via 2 x large grills in the rear wall and grills in the plantroom door. The grills in the wall and the door are at both high and low levels and communicate directley to outside. The ventilation is more than adequate, as measured and calculated . Vermin mesh is fitted to the grills in the wall , this 10 mm in diameter. The 3 x boiler modules are connected their own manufacturer specific, plastic flue manifold system. Holes had been drilled into the manifold, to allow GFA readings to be carried out . This is unnecessary as there is sample points supplied by the manufacturer, on the front of the heat ex . I have fitted Regin test point plugs , to holes drilled as req ( made good ) The flue manifold is then connected to a stainless flue , suspended from the ceiling. There has been numerous repairs carried out to the flue , prior to my visit . These repairs are only meant as a temporary measure and not a permanent fix . There is condensate stains to the concrete floor below the flue repairs , indicating that the joints have been repaired . The repairs are not leaking currently, but these can only get worse with time. I highly recommend instructing a flue specialist, to split the flue and replace the wet seals. The flue has non mechanical traps fitted to its condensate lines . The flue then enters an purpose built external brick build chimney, the terminal can be seen clearly . A liner has not been used , as I can see individual flue lengths ( looking from below ) As this is not passing through the building itself , but on an external wall . This is still a cause for concern as the flue joints cannot , be visually inspected as per BS6644. There is an emergency stop button at the plantroom door , when pressed the gas supply is isolated to the area via a solenoid valve. The controls are auto resetting and not manual , this is an existing installation. The gas supply enters the area at low and sleeved through the wall , from the external boundary meter . The sleeve is not sealed and does not fully protrude in the plantroom. There is a gas AECV fitted upon entry for localised isolation purposes. Pipe work is fully identified and well supported along its route . Purge and test points are fitted throughout, with a gas ECV to each module . Tested working pressure , and found to be ok . Appliance details Module 1 top Hamworthy Fleet F125V Sn , F12VM261GB 02298H 125 kw not rated GFA High fire 02 , 5.1 Co2 , 9.0 Co , 101 ppm Ratio , 0.0011 Low fire 02 , 5.2 Co2 , 8.9 Co , 23 ppm Ratio , 0.0003 Module 2 middle Hamworthy Fleet F125V Sn , F12VM161GB 02297H 125 kw not rated GFA High fire 02 , 5.1 Co2 , 9.0 Co , 62 ppm Ratio , 0.0007 Low fire 02 , 5.1 Co2 , 9.0 Co , 3 ppm Ratio , 0.0000 Module 3 bottom Hamworthy Fleet F125V Sn , F12VM161GB 02296H 125 kw not rated GFA High fire 02 , 5.1 Co2 , 9.0 Co , 72 ppm Ratio , 0.0008 Low fire 02 , 5.1 Co2 , 8.9 Co , 14 ppm Ratio , 0.0002 The gas meter (U65) is a boundary meter , located in the front garden area of the building . Its is housed in a purpose built plastic meter house , with ventilation and a lockable door . The gas transporters warning advice label is present and completed . Both the ECV and AECV are smooth operating, complete with labels of operation . The gas pipework from the meter to the plantroom , is ran below ground level . The pipe work emerges from the ground to enter the plantroom , through a tarmac path . I cannot see any type of protection on or around the pipe, to protect . The pipe work then enters the plantroom, its sleeved but not sealed . Pipe work is fully identified. Carried out commercial gas tightness test as per the guidance published in UP1A. Traced the pipe work along its entire route as best as possible , then calculated the total volume . IVP - 0.198 m3 IVF - 0.0197 m3 IMV - 0.0100 m3 Total - 0.3179 m3 S.O.S - the plantroom > 60 m3 MAPD - 3.9 mb Letby - 2 minutes Stabilisation - 6 minutes TTP - 2 minutes Result... Pass , zero drop recorded or detected with appliances connected. LPC 19.4.21 1350 - 1620 Attended site and carried mechanical check on components etc. Found that expansion vessel to LHS Calorifior to have a leak present in pipe work , repaired as req but corrosion present . Found leaking fitting again to RHS Calorifior on destrat circuit repaired but corrosion present . Tested and check rest of equipment all ok .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5707
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5707
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5707
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5707
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5707
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes