## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Emmerson Court
Shiremoor
Newcastle Upon Tyne
NE27 0NG
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 20-5708
DATE OF REPORT: 27/04/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5708
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Emmerson Court
Shiremoor
Newcastle Upon Tyne
NE27 0NG
Carried Out On | 26/04/2021, 27/04/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 27.05.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5708
SECTION 3: Report
LPC 26.4.21 1345 - 1630 Attended site and carried out commercial gas tightness test, as per the guidance published in UP1A. The gas meter is located in a brick build out building , at the front of the main building. The gas meter is sitting on a combustable material (wood) A metal louverd is present for ventilation to the area , the key is clearly labelled. Both the ECV and the AECV are free moving and fall the closed position, the main ECV does not have a label of operation attached to it. The fas transporters warning advice label is not present next to the meter . Earth bonding is present to within the outbuilding . Gas pipe work from the meter to the building, is sleeved with a non metallic material ( plastic soil pipe ) also not sealed . The gas pipe work then enters the building in a sealed duct , between flats 12 & 11 . Pipe works then breaks through to the main hallway area , where it above a suspended tiled ceiling . The gas supply is ran in 3 " steel pipe work , that is mostly unidentified along its route , joints are welded as req Pipe work then enters the plantroom area at high level , no sleeved through the wall but sealed with fire sealant . There is an emergency stop button at the plantroom door , when pressed the gas supply is isolated to the area via a solenoid valve. The gas solenoid valve is located above the gas meter , not in the plantroom. The controls are auto resetting and not manual , this is an existing installation. There is a gas ECV fitted upon entry to the plantroom, for localised isolation purposes. Pipe work within the plantroom is partly identified , but well supported , with purge and test points fitted . Located the gas pipework within suspended ceiling, traced along its entire route . Calculated the volume inorder to carry out the test. IVP - 0.243 m3 IVF - 0.0243 m3 IMV - 0.067 m3 Total - 0.3343 m3 S.O.S - the plantroom - 50 m3 MAPD - 3.9 mb Result... Pass , zero drop recorded or detected with appliances connected. Found installation to be AT RISK and a warning notice has been issued. Unable to reduce the risk as no drop on pipe work gas tight . Client to contact their gas supplier , to supply a completed warning advice label and attach label of operation to ECV. Boiler modules not worked on or tested today . LPC 27.4.21 1220 - Attendee site and carried annual commercial gas saftey inspection as req , on 3 x open flue boiler modules. Modules have been tested as per manufacturers instructions, to ensure safe operation with all 26.9 checks along side . Only able to test modules 1 ( top) and 2 ( middle) as module 3 ( bottom ) not running possible LMU fault . Burners have not removed as GFA readings well within manufacturers specifications ( Gaskets etc have not been replaced ) Ventilation for combustion and cooling purposes is supplied via, 2 x large metal Louvred doors. Both doors communicate directley to outside, they do not have a true high and low definition ( just vertical strips) Vermin mesh is present in the internal side of the door , this is over 5 mm in diameter. Found doors to supply more than adequate ventilation to the area, with the appliances currently installed. The 3 x modules are connected to a manufacturer specific, plastic flue manifold assembly. Holes had been drilled and taped over to carry out GFA , there is a supplied test point at the front of the appliance. I have fitted a Regin flue sample plug to each hole drilled as req . The manifold is then connected to a stainless steel flue , that is suspended from the ceiling. The had mechanical traps fitted to the condensate lines , that I have removed today and replaced with non mechanical traps . I have also cut out leaking condensate pipe work and replaced as req . There is a lot of corrosion around the rear of the modules , below the traps and flue . I have repaired these leaks today , but the damage has already been done . The way the condensate lines have been installed , is very poor and offers no support to traps. The traps can become heavy when full of condensate . I would definitely recommend that the new traps are fitted to the modules themselves, and that the condensate lines are repiped. The flue is good visual condition with no signs of corrosion or leaks present , at time of visit within the plantroom . The stainless steel flue then exits the plantroom at high level , passes through vertically to the floor above . The flue does not have a fire stop fitted around it , just a hole in the concrete floor . The flue then passes through a false wall / duct, in the quiet lounge above . The ducting does not have inspection hatches fitted . Then finally through the roof space above , the flue terminal can clearly be seen . I have not been able to gain access to the flue in the loft , due to the roof spar configeration . The lack of fire protection, inspection hatches and finally loft access , are all causes for concern . As per unsafe situations only RS flue req inspection hatches along its route . I highly recommend having these issues tending to and being resolved . Appliance details Module 1 top Hamworthy Fleet F125V Sn , F12VD151GB 01371G 125 kw not rated GFA High fire 02 , 5.1 Co2 , 9.0 Co , 71 ppm Ratio , 0.0008 Low fire 02 , 5.0 Co2 , 9.0 Co , 5 ppm Ratio , 0.0001 Module 2 middle Hamworthy Fleet F125V Sn , F12VD151GB 01370G 125 kw not rated GFA High fire 02 , 5.1 Co2 , 9.0 Co , 77 ppm Ratio 0.0009 Low fire 02 , 5.1 Co2 , 9.0 Co , 20 ppm Ratio , 0.0002 Module 3 bottom Hamworthy Fleet F125V Sn , F12VD151GB 01369G Not tested as not running . Reqs investigation to identify fault .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5708
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5708
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5708
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5708
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5708
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes