## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Feetham Court
Forest Hall
Newcastle Upon Tyne
NE12 9QJ
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 20-5710
DATE OF REPORT: 21/04/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5710
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Feetham Court
Forest Hall
Newcastle Upon Tyne
NE12 9QJ
Carried Out On | 21/04/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 05.05.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5710
SECTION 3: Report
LPC 19.4.21 0840 - Attended site to carry out commercial gas tightness test, as per guidance published in UP1A. The gas meter is a boundary meter , located in a build built housing at the front of the building . The housing has a locking door and a locking gate for access . When I gained access to the gas meter , I could immediately smell gas . I sprayed the fitting with LDF , found the spindle to be leaking on the wheel head type ECV. With the ECV now in the off position, I carried out a letby test to test before reporting the issue. The ECV is letting by at a large rate , within 45 seconds it the gauge displayed an increase of 2 mb I have informed northen gas networks emergency line on 0800 111 999 , their ref no given - 5370 3307. Waited for engineer to arrive , who accessed the situation and called in another non domestic engineer to assist . I was asked to waite until the other engineer to arrive , to show him the site ( plantroom , gas run etc) Handed over to non domestic engineer, who is going to attempt to repair the valve . All failing a new gas valve may have to ran in to the meter , with an upgraded ECV. I have informed the site manager , and she is aware of the situation. The outlet sidd of the gas meter has been kept pressurised , boilers off via isolaters , to prenve line having to be purged. LPC 21.4.21 0825 - 1455 The Gas Transporters ECV has now been repaired by Northern Gas Networks . Carried out commercial gas tightness test as per guidance published in UP1A. Pipe work from the gas meter over 2 " , not welded but threaded fittings . The gas meter door cannot be locked as the door has warped, the gate in front of the meter cupboard is locked The key for the gas meter is clearly identified. There is a lot of rubbish , debris within the gas meter housing that is combustable. The items of rubbish will req removal by a professional , as there is medical supplies outside the door and possibly internally . I have taken the straightest route of the pipe work that is ran below ground level, I can pressume its route as no line diagram on site . The gas transporters warning advice label is present and completed. The Main ECV and the AECV do not have labels of operation present . Gas pipe work is fully identified where visable , I can see a taped product on the pipe work for protection ( passes through concrete slab. The pipe work then enters the plantroom at low level through the wall , not sleeved but sealed. Gas ECV fitted upon entry for localised isolation purposes, purge and test points present . Each appliance has it's own manufacturers isolation valves fitted . Earth bonding present upon entry to plantroom. There is an emergency stop button at the plantroom door, when pressed the gas supply is isolated to the area via a solenoid valve. The controls are auto resetting and not manual, this is an existing installation. IVP - 0.378 m3 IVF - 0.0378 m3 IMV - 0.100 m3 Total - 0.5158 m3 S.O.S - the plantroom > 60m3 MAPD - 3.6 mb Result .... Pass , zero drop recorded or detected with appliances connected. Warning notice issued as 3 " steel pipe work not welded but threaded joints/ fittings . Combustable rubbish in gas meter housing . Whilst on site carried out annual commercial gas saftey inspection , on 3 x open flue Remeha boiler on a shared flue . Each appliance has been tested for safe operation as per manufacturers instructions, with all 26.9 checks along side. Boilers 1 + 3 have had their burners removed eith Gaskets etc replaced . The burner is boiler no.3 is damaged on the end . Boiler no.2 ( middle ) has only just been replaced and has not been opened up for inspection . The wiring to the new appliance ( no.2 middle ) has not been fully completed , and linked to the BMS. Boiler no.3 RHS has a lot of corrosion internally consistent with a leaking inner flue . It's clear to see that a new inner flue has been installed , not leaking now . When I carried out the GFA on the appliance, I could not get the gas valve to tune / settle . I have not been able to achieve acceptable GFA readings as per manufacturers instructions. Found the appliance to be AT RISK gas and electric supply isolated , warning label attached and notice issued. All 3 x appliances are connected to a common flue system , that is suspended from the ceiling. There are numerous signs of previous repairs along in length , none of the repairs are leaking at time of testing. There is numerous signs of corrosion on the flue , but again these are not leaking at the moment . I would highly recommend a flue specialist to attend site , split all flue joints and replace wet gaskets as req. The flue has various condensate lines fitted, all have non mechanical traps in place. The flue enters a brick built chimney , I do not know if the chimney is lined or not . The flue terminal is clearly visable fro the rear of the building . Ventilation for combustion and cooling purposes, is via 2 x large metal Louvred doors. Doors do not have a true high and low definition . Both doors communicate directley to outside, without any fly screens in place. Doors supply adequate ventilation for safe operation of the appliances installed , as measured and calculated . Appliance details Boiler 1 LHS Remeha Quinta 115 Sn , 0920207024750 115 kw , not rated GFA High fire O2 , 5.3 Co2 , 8.9 Co , 52 ppm Ratio , 0.0006 Low fire O2 - 4.9 Co2 , 9.1 Co , 12 ppm Ratio , 0.0001 Boiler 2 middle Remeha Quinta ACE 115 Sn , 2014623821200 115 kw , not rated GFA High fire O2 , 4.7 Co2 , 9.2 Co , 62 ppm Ratio , 0.0007 Low fire O2 , 6.1 Co2 , 8.4 Co , 11 ppm Ratio , 0.0001 Boiler 3 RHS Remeha Quinta 115 Sn , 090207025150 115 kw , not rated Left isolated as new gas valve req . Found both DHW expansion vessels to have no charge , used compressor and recharged to correct pressure . Foynd that the control rod on the 2 port valve , to Calorifior 1 LHS is missing and spindle wedged in .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5710
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5710
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5710
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5710
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5710
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes