## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Spring View
Bristol Drive
Battle Hill
NE28 9RN
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 20-5711
DATE OF REPORT: 23/04/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5711
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Spring View
Bristol Drive
Battle Hill
NE28 9RN
Carried Out On | 22/04/2021 23/04/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
AGSC TD 27.05.2021

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5711
SECTION 3: Report
LPC 22.4.21 1405 - 1520 Gas tightness test as per guidance published in UP1A The gas meter ( G25/U40 ) is boundary meter that is located in a purpose built plastic housing . The housing is kept locked and has ventilation fitted . There are plants around the meter housing, these are kept trimmed back allow access . Site is aware of the gas meter location , there are numerous photos around the building , showing location of gas meter . Gas transporters warning advice label , is present and completed. Both the ECV and the AECV are free moving, complete with labels of operation. The line diagram on site is very limited, and only show the pipe work route within the plantroom . I have measured and walked the straightest route of the pipe work , I can assume this is the logical route. The pipe work leaves the gas meter in 2 " steel , but emerges outside the plantroom area in 5 " steel. The calculation has been calculated using the 5 " steel as the pipe work volume . LPC 23.4.21 0830 - 1500 Pipe work enters the plantroom at low level , sleeved and sealed through wall . Wheel head type ECV fitted upon entry for localised isolation purposes. Pipe work is fully identified and well supported along its route . Each appliance has it's own fitted, test and purge points present . There is an emergency stop button at the plantroom door , when pressed the gas supply is isolated to the area via a solenoid valve. The controls are auto resetting and not manual , this is an existing installation. IVP - 0.77 m3 IVF - 0.077 m3 IMV - 0.067 m3 Total - 0.914 m3 S.O.S - the plantroom - > 60 m3 MAPD - 2.6 mb Letby - 4 minutes Stabilisation - 6 minutes TTP - 6 minutes Result ..... Pass , zero drop recorded or detected with appliances connected. Whilst on site carried out annual gas saftey inspection as req , on 2 x open flue water heaters and 3 x open flue boiler modules . Each appliance has been tested to ensure safe operation as per manufacturers instructions , with all 26.9 checks along side. Burners have not been removed or gaskets replaced, as GFA reading well within manufacturers specifications. Cause for concern the plantroom walls are wooden lined , I do not the fire rating of the product etc . The client will have the data for the fire resistant quality of the product , I cannot comment further. Ventilation for combustion and cooling purposes is supplied via, 2 x metals grills in the wall at high and low levels . Both Vents communicate directly to outside, with vermin mesh present that is 10 mm in diameter. The ventilation installed is only just sufficient for combustion purposes, but does not offer any for cooling . The ventilation does not comply with BS6644, this is not AT RISK but is a cause for concern/ not to current standards. The 2 x water heaters are connected to a common flue system , that is suspended from the ceiling. The flue has non mechanical traps fitted to the condensate lines . The flue then enters a brick built external chimney , flue is sealed into the chimney . Flue terminal is visable from the front of the building I do not know if a flue liner has been used or not . The 3 x boiler modules are connected to a manufacturers specific plastic flue manifold system. Each module has its own non mechanical bottle trap fitted. The flue manifold is then connected to a stainless steel Flue , that is is also suspended from the ceiling. The flue has non mechanical traps fitted to the condensate lines. The enters the same brick built external chimney, and is sealed . I do not know if a flue line has been used or not , flue terminal is visable from the front of the building . Holes had been drilled in the plastic manifold , for taking GFA and taped over . There is purpose provided sample points on the front of the appliance , at low level . I have fitted 3 x Regin flue sample plugs , to holes as req . Appliance details Water heater 1 RHS Lochinvar SHW 46 325 NG CE Sn , 1605102536780 40 kw , not rated GFA High fire O2 , 5.0 Co2 , 9.0 Co , 41 ppm Ratio , 0.0005 Low fire 02 , 5.6 Co2 , 8.7 Co , 19 ppm Ratio , 0.0002 Water heater 2 LHS Lo hinvar SHW 46 325 NG CE Sn , 3815102002513 40 kw , not rated GFA High fire O2 , 4.8 Cow , 9.1 Co , 60 ppm Ratio , 0.0007 Low fire 02 , 5.2 Co2 , 8.9 Co , 22 ppm Ratio , 0.0002 Boiler module 1 top Hamworthy Fleet F50V Sn , F5VA161GB 02346H 50 kw , not rated GFA High fire O2 , 5.0 Co2 , 9.0 Co , 22 ppm Ratio , 0.0002 Low fire 02 , 5.1 Co2 , 8.9 Co , 7 ppm Ratio , 0.0001 Boiler module 2 middle Hamworthy Fleet F50V Sn , F5VA161GB 02345H 50 kw , not rated GFA High fire O2 , 5.1 Co2 , 9.0 Co , 35 ppm Ratio , 0.0004 Low fire O2 , 5.0 Co2 , 9.0 Co , 26 ppm Ratio , 0.0003 Boiler module 3 bottom Hamworthy Fleet F50V Sn , F5VA161GB 02344H 50 kw , not rated GFA High fire O2 , 5.1 Co2 , 9.0 Co , 17 ppm Ratio , 0.0002 Low fire O2 ,5.0 Co2 , 9.0 Co ,26 ppm Ratio , 0.0003

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5711
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5711
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5711
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5711
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5711
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes