## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
The Elms
Chester-Le-Street
County Durham
DH2 3EJ
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 20-5813
DATE OF REPORT: 05/02/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 20-5813
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | The Elms
Chester-Le-Street
County Durham
DH2 3EJ
Carried Out On | 18/12/2020, 21/12/2020, 22/12/2020, 05/02/2021
Survey Completed By | Lee Chatterton
SECTION 2: Introduction
Repair leaking pipe on flue as per Jim Park at Karbon Homes

## Report
ZENITH MECHANICAL SERVICES
Report Number | 20-5813
SECTION 3: Report
LPC 18.12.20 0830 - 1035 Arrived on site and gained access to plantroom area . Shut down all boilers and CHP unit , to allow inspection on flues externally as reported leaking . Located and identified leaking to become coming from the external condensate condensate connection on the CHP unit flue . Attempted to repair but due to external temperature and the dew point of the flue gasses , joint permanently wet and cannot seal. CHP will be left isolated over the weekend to allow the flue internally to dry . I will return to site on monday of next week and carry out the repair . Whilst I was on site I cut in a deep seal trap on the condensate line from all 5 x boilers, this is now complete . Boilers have not been physically worked on or tested today. LPC 21.12.20 0820 - 0905 Arrived on site and carried out repair to eternal leaking , condensate line on flue from CHP unit. Appliance left isolated as silicone will req time to fully cure to provide a good seal. I will call back to site tomorrow and put the CHP back into use . LPC 22.12.20 1305 - 1400 Arrived on site and gained access to the plantroom area. Reinstated the CHP unit and monitored the external flue repair . After about 15 -20 minutes the seal failed and began leaking condensate again. Isolated CHP and made safe , the flue will req physically splitting and either a new drain fitting or possibly can internal seal. There isn't a locking nut externally on the thread, to allow adjustment . Dave Hunter aware of situation. LPC 5.2.21 0825 - 1140 Attended site and looked at the new flue condensate connector size , installed by flue contractor . Left site and called to suppliers to collect relevant materials , proceeded back to job. Gained access to plantroom area , fitted new condensate line to external flue for CHP unit. Reset CHP and started up unit , monitored functions and performance. Allowed time for trap to fill whilst being monitored, found new condensate to be ok now as not leaking . Photos sent direct to Dave Aston .

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 20-5813
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5813
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5813
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5813
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 20-5813
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes