## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Phoenix Rise
Ambassadors Way
North Sheilds
NE29 8SQ
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 21-10561
DATE OF REPORT: 14/09/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-10561
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Unit 1 Hunslet Trading Estate
Servern Way
Hunslet
Leeds
LS10 1BL
Site Address | Phoenix Rise
Ambassadors Way
North Sheilds
NE29 8SQ
Carried Out On | 09/09/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
6 Monthly Mechanical Check

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-10561
SECTION 3: Report
Attend site 0930 to carry out 6 month mechanical check 3 x hamworthy fleet f 85v heating boilers inspected for leaks and operational checks all ok no issues 1 x grundfos magna 3d 65-150 f340 twin set zone 1 heating pumps operational check all ok no issues 1 x grundfos magna 3d 40-150 f 250 twin set zone 2 heating pumps operational check all okno issues 1 x wilo comfort p235 pressurisation unit for heating operational checks all ok no issues 1 x zilmet 500l heating expansion vessel isolated drained and pressure set at 1.5 bar 2 x schnider m700 s2 srsu zone actuators zone 1 ok no issues zone 2 has linkage disabled so is permanently on 2 x lockinvar shw61- 325 gas fired hot water heaters operational checks both ok no issues 1 x grundfos ups 15-50 n 130 dhw pump 2 x grundfos mge 90ld heating shunt pumps operational check ok but noisey 2 x grundfos mge 90 sc primary pumps operational check ok no issues 1 wilo comfort p235 pressurisation unit for ASH operational check ok no issues 1 x zilmet 50l expansion vessel found to be flat isolated and drained and recharged but find schroder valve leaking so replaced with new and recharged vessel to 1.5 bar All pipework in good condition All lagging in good condition Condensate pipe off lochinvar boilers leaking round by the gas solinode valve this will need replacing Parts required 2 x 11/4" 45° elbows 2 x 11/4" sockets 11/4" solvent weld pipe Offsite 1230 complete

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-10561
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-10561
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-10561
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-10561
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-10561
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes