## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Chapelville
Front Street
Seaton Burn
NE13 6EH
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 21-11295
DATE OF REPORT: 01/10/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-11295
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Chapelville
Front Street
Seaton Burn
NE13 6EH
Carried Out On | 28/09/2021, , 30/09/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
No hot water on site - faults on pumps. 1st phase of the building is all on apart from 1. 2nd phase, 7 people have no hot water, or temperature is intermittent. ASHP pump is in fault - red light on. 1 Boiler is 23dgs and other is 26dgs

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-11295
SECTION 3: Report
Attend site 1400 Check boiler room reset ASH pump but no issues with the dhw in plantroom, Go into flat 3 and check hot water Find all hot water pipework cold suggesting a mixing shower or a tmv passing strip down shower and test but find ok strip out pedestal on hand basin and check tmv but find all ok reassemble sink pedestal do the same in flats 4,5,6,9,10,11 but no faults found need to return tomorrow to check the remaining flats to find the faulty mixing valve Offsite 1700 Attend site 0800 Find flats 3,4,5,6,9,10,11,12,13,22,23,24and 25 have no hot water Isolated cold water to each flat run hot water until all hot then one by one turn on the cold water and check dhw pipework temp to se if it drops , flat 12 and flat 24 were found to have faulty tap mixing valves and the cold water is passing into the hot water pipework chilling it down so isolated the taps and karbon are going to attend to replace. A pressure reducing valve could be fitted to the cold water main coming into the plantroom sothe whole site is balanced and this would eliminate this issue. Flats 3 and 10 the cold water gate valves had to be replaces as they snapped in the closed position they were replaced with quarter turn valves I needed assistance as this needed the site mains cold water turning off and draining down once the work was completed the mains cold water was turned back on and vented Parts used 1 x 22mm pressfit isolation valve 1 x 22mm pressfit slip connector 1 x 22mm pressfit isolation valve( from van stock ) £18 Offsite 150 complete

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-11295
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-11295
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-11295
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-11295
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-11295
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes