## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Castle Court
Annfield Plain
Stanley
DH9 7SA
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 21-11684
DATE OF REPORT: 13/10/2021
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-11684
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Castle Court
Annfield Plain
Stanley
DH9 7SA
Carried Out On | 13/10/2021
Survey Completed By | Dave Aston
SECTION 2: Introduction
No radiators working in communal area as reported by Debbie Kennedy - Scheme Manager ---- Zenith attended Job A0983100 on 11/10 but radiators have gone straight back off and will not come on again today ---- ---- No Covid isssues

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-11684
SECTION 3: Report
Re attend for no heating Find no1 boiler off on E112 no 2 boiler off on E25 Both thes faults are faults on temperature differences between flow and return check all pipework for a strainer and clean find no1 heating pump siezed it's a basic car.s1this needs replaced. Also the pressurisation unit is faulty this is a flexifil unit this needs replacing. Reprogram rhe working heating pump to increase the flow rate which stops the boilers going off on flow return temperatures being so far apart. Check with a multimeter resistance of all thermisters which are all within manufacturer's tolerances All working when I left 1500

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-11684
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-11684
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-11684
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-11684
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-11684
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes