## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Windsor Grange
Windsor Drive
Howdon
NE28 0NP
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 21-12997
DATE OF REPORT: 04/04/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 21-12997
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Windsor Grange
Windsor Drive
Howdon
NE28 0NP
Carried Out On | 05/01/2022
Survey Completed By | Andrew Diffley
SECTION 2: Introduction
6 Monthly Mechanical Check

## Report
ZENITH MECHANICAL SERVICES
Report Number | 21-12997
SECTION 3: Report
2 x Hamworthy Fleet F175v heating boilers operational check all OK 2 x Lochinvar SHW60-325CE water heaters operational checks all OK 1 x Wilo 200 litre expansion vessel. Isolated drained and charged to 1.5 bar 1 x Wilo 50 litre expansion vessel. Isolated drained and checked at 1.5 bar 2 x Global Water potable expansion vessels. Isolated drained and charged to 1.9 bar 2x Schneider M700 DN65 three port and actuator operational check all OK 2 x Wilo Comfort P135 pressurisation units operational check all OK 2 x Magna 3D 40-150 twin seat heating pumps both OK 1 x Wilo DP-E40 150- 3/2 twin set ASHP Primary pump operational check all OK 1 x Magna 3D 32-80 twin set ASHP secondary pump operational check all OK 1 x Grundfos UPS 15-50 N 130 Selectric Stainless secondary DHW circulator working ok Flues in good condition Lagging in good condition Pipework in good condition. Isolated minor corrosion Damage to Wilo DP-E40 fan cover

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 21-12997
SECTION 4: Photos
Room / Area
Plant room
Description
Wilo pump damage
Notes
Room / Area
Description
Notes
Room / Area
Plant room
Description
Lochinvar no2 inlet elbow
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-12997
SECTION 4: Photos
Room / Area
Plant room
Description
Lochinvar no 2 tundish
Notes
Room / Area
Plant room
Description
Lochinvar no2 flue condensate
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-12997
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-12997
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 21-12997
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes